- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Structured Cabling Systems supporting the following network topologies; Ethernet 10BaseT, 100BaseT, and 1000BaseT standards including outlet plates, structured grade unshielded twisted pair (UTP) cables, shielded twisted pair (SFTP) cables and fiber optics cables (FO).

          - Electrical systems including rough-in, pathways, conduit, boxes and backboards.

          - FTTO Switch, Power supply, SFP Requirements

      - REFERENCES

        - ANSI/TIA-568-C: Generic Telecommunications Cabling for Customer Premises, published 2009.

        - ANSI/TIA-568-C.1: Commercial Building Telecommunications Cabling Standard, 2009.

        - ANSI/TIA-568-C.2: Balanced Twisted-Pair Telecommunication Cabling and Components Standard, 2009.

        - ANSI/TIA-568-C.3: Optical Fiber Cabling Components Standard, 2008.

        - ANSI/TIA-862: Building Automation Systems Cabling for Commercial Buildings, 2002.

        - ANSI/TIA-569-B: Commercial Building Standard for Telecommunications Pathways and Spaces.

        - ANSI/TIA-606-A: Administration Standard for Commercial Telecommunications Infrastructures, 2002.

        - ANSI/TIA-758-A: Customer-owned Outside Plant Telecommunications Infrastructure Standard, 2005.

        - International Standards Organization/International Electro Technical Commission.

        - ISO/IEC11801, Amendment 1, 2009: Generic Cabling for Customer Premises, Class EA.

        - Underwriters Laboratories (ULÒ) Cable Certification and Follow Up Program.

        - ANSI J-STD-607-A, Commercial Building Grounding (Earthing) and Bonding Requirements for Telecommunications.

        - BICSI Telecommunications Distribution Methods Manual 12th Edition.

        - NECA / BICSI 568 Installing Commercial Building Telecommunications Cabling.

        - UL 910, Test for Flame-Propagation and Smoke Density Values for Electrical and Optical Fibre Cables in Spaces Transporting Environmental Air, 1997.

        - UL1685, Vertical-Tray Fire Protection and Smoke Release Test for Electrical and Optical Fibre Cables.

        - IEEE.1100-2005, Powering and Grounding of Electronic Equipment.

        - BS 7671.

        - IEC.

        - ISO/IEC 11801- 2nd Edition, Amend 2: 2010: Information technology - Generic cabling for        customer premises

        - ISO/IEC 18010:2002, Information technology – Pathways and spaces for customer premises Cabling

        - ISO/IEC TR 14763-3, Information technology – Implementation and operation of customer        premises cabling – Part 3: Testing of optical fibre cabling

        - ISO/IEC TR 14763-2, Information technology – Implementation and operation of customer       premises cabling – Part 2: Planning and installation.

        - Local Codes and Standards.

        - Local telecom service provider regulations and requirements.

      - SYETM DESCRIPTION

        - The communication cabling network specified under this section shall serve the project Local Area Network (LAN) for computers, Voice over Internet Protocol (VOIP), data system … etc Networks within the building.

        - The communication cabling network shall provide end-to-end connectivity from a network PC, VOIP telephone, etc to respective server.

        - The communication cabling network horizontal cabling of all networks shall be identical with CAT6 UTP cables (SFTP for data outlets) and RJ45 outlets for each system component.  Locations of RJ45 outlets are as indicated in the layout drawings. However, Contractor shall allow for few additional outlets if required, as an outcome of detailed engineering of other low current systems by the proposed specialist’s vendors.

        - Horizontal cables from all systems components shall be terminated at RJ-45 FTTO switches for data. All systems FTTO switches shall be located in proper location based on manufactures requirement in each floor, to allow flexibility in converting outlets from any system to another, as required in the future.

        - Systems Backbone cable shall be multi-mode multi strands (OM3) fiber optic (FO) cables as indicated in drawings and shall originate from the Main Data Hub in the server room.  Fiber optic cables shall be terminated at both ends by suitably sized fiber optic patch panels. FO patch panels shall be housed in the same 19” equipment cabinet as RJ45 patch panels in server room.

        - Contractor shall ensure that no horizontal cable run from patch panel to outlet exceeds 90m being the Cat-6A limits. In the event of any outlets exceeding the limit Contractor shall allow for 2 strand multi-mode FO cable including suitable FO outlet to RJ45 outlet convertor.

        - On completion of installation, specialist shall test all fiber optic cable runs using (CAT 6a) cable links with suitably rated scanners, and test results shall be submitted to Engineer.

        - Labeling of outlets and connecting hardware:

          - Identify each outlet and associated termination point on the blocks with the following label format. Labeling shall be by a permanent labeling method. The room number identification shall be the final room number provided by the Engineer.

          - Closet number, followed by a dash and room number, followed by a dash and number of outlet in room (if multiple outlets are in the room):

            - Closet end: Sample A-205-V 2: closet A - location 205 - Structured cable No. 2.

            - Outlet end:

              - Sample B-205: closet B - location 205

              - Identify individual jacks on each plate with outlet type and number, if multiple outlets occur in the room: label adjacent to each outlet with a "V", "D" for each structured outlet… Etc.

          - Color code for outlets shall be as follows: Structured jacks yellow jack inserts

          - The outlet plate labeling shall be engraved, 5 mm high, onto the cover plates and black filled.  No other labeling method is acceptable for the device outlet plates.

        - Provide fire stop at all penetrations through fire rated walls and ceiling/floor systems designated for technology use.  Fire stopping method shall meet or exceed the minimum rating of the wall, ceiling or floor penetrated.

        - Coordinate the installation of the technology outlets in the modular furniture with the Supplier of the furniture; all wiring is to be installed in the modular furniture raceway.  Provide all cover plates (RJ45 outlets) for the technology outlets.  If cable is exposed from wall outlet to furniture base, provide a flexible protective cover of round plastic sheathing.

        - Client Expectation:

        - The Contractor shall provide a method statement for each of the system performance criteria to illustrate how these requirements will be met for each of the equipment/materials being proposed.

        - Electromagnetic Compatibility:

          - All equipment and systems installed under this Contract shall meet following specifications on electromagnetic compatibility:

            - Interference immunity according to BS EN 61000: Part 6-3

            - Emitted interference according to BS EN 61000: Part 6-2

        - Interface to other systems: Communication Services cabling shall be interfaced to BMS, fire alarm system, security systems and other low current systems as shown on the drawings.

      - SUBMITTALS

        - Furnish complete sets of shop drawings for the proposed system.  The submittal shall be neatly bound in a three ring or comb type binder, with protective covers.  The cover must identify the project, system, date and vendor name.  The submittal shall consist of, but not be limited to the following items:

          - Title sheet showing the Contractor's name, address, phone number and date submitted.  Clear area shall be provided on the title sheet for shop drawing review stamps.

          - Material list showing quantity, manufacturer and description of each item being furnished.

          - Engineered riser diagrams showing all distribution equipment, connections and calculated tap values and signal strength levels at each device and outlet.

          - Product data sheets with complete technical data for each item being furnished.

        - Method statement for system’s component installation, testing and commissioning.

        - Compliance with Project Specifications:

        - The Contractor shall comply fully with all requirements issued in the Contract and provide a full compliance matrix with proof of compliance. Partial Compliance and non-compliance must also be documented.

        - Compliance with Local Authority Requirements:

        - The Contractor shall comply with local authority requirements where these take precedence over the Project specifications. Where the Contractor deters from this course they are responsible for obtaining approvals from the relevant authorities to change the requirement.

        - Prepare shop drawings and product data sheets, as well as 3rd Party certificates (refer to Manufacturer Qualifications 3.4) for technology equipment with adequate details and scales as necessary to clearly show construction Indicate operating characteristics for each required item and design conditions.

        - Submit the actual cable test data as generated by the manufacturer for the stock to be utilized for construction. Contractor shall review each submittal prior to submission, and check for compliance with Contract Documents.

        - Corrections shall be noted. Mark with approval stamp prior to submission.

        - Submittals that do not bear Contractor’s approval stamp will be returned without action.

        - Shop drawings and product data shall include, but not be limited to:

          - Copper Cabling.

          - Fibre Cabling.

          - Coaxial Cabling.

          - Low Voltage Protection Devices.

          - Fibre Connector Housings.

          - Faceplates.

          - Jacks.

          - Modular Patch Panels.

          - Wiring blocks and other connection details.

          - Racks.

          - Cable Tray.

          - Cable Runway.

          - Firestop Details.

          - Technology earthing systems description and materials.

          - CATV/Broadband Distribution System Components.

        - The submittals shall be reviewed only for general compliance and not for dimensions, quantities, etc. The submittals that are returned shall be used for procurement. The responsibility of correct procurement remains solely with Contractor. The submittal review shall not relieve Contractor of responsibility for errors or omissions and deviations from the Contract requirements.

        - Equipment substitutions are prohibited. If the submittal shows variations from the requirements of the Contract Documents for any reason, Contractor shall provide written detail of each variation in the letter of transmittal.

        - Contractor shall note in red on the submittal any change in design or dimension on the items submitted including changes made by the Manufacturer that may differ from catalogue information.

        - Shop Drawings shall be submitted in an electronic format on CD. The file format shall be Adobe portable data file (pdf) or provide software to enable viewing of files of the other formats at no additional cost to Employer.

        - The Manufacturer is to provide printed or electronic independent 3rd Party certification certificates (such as ETL Laboratories) for Category 6, Class E Channels to both ISO and TIA standards according to the full standards defined channel model (4 connectors over 100  metres). Test Certificates for both long and short channel Configurations to be submitted.

        - Provide samples of all proposed cables, connectors, fittings, accessories, ..etc together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations and sizes of pathways and outlets.

      - QUALITY ASSURANCE

        - Perform Work in accordance with reference standards listed in this section.

      - QUALIFICATIONS

        - Contractor Qualification:

          - For the following items Contractors shall provide written confirmation and documentary proof with their bid response, failure to adhere to this will lead to disqualification from the bid submission.

          - Contractor shall be fully qualified to perform installations as described on the Drawings and within these Specifications. The following qualifications apply to all Work unless otherwise noted. Employer reserves the right to wave any or all of these requirements.

          - Contractor shall have been active in bidding, being awarded, and performing Work consistent with that indicated on the Drawings and in the Specifications for a period not less than five (5) years. The Contractor is to provide a list of projects undertaken in the last 1 year, with the customer contact and references provided.

          - Contractor shall possess current training and certifications by the specified manufacturers for the installation and maintenance of the low voltage cabling systems, including firestop systems. Furthermore Contractor must possess all respective certifications prior to bidding any project.

          - Certifications which are Employer specific and not global shall not be recognized by Employer. The Contractor is to provide printed copies of each certified Engineer employed by the Contractor. The Contractor is to provide a letter from the Manufacturer confirming the Technician Name, Company Name, Course Trained, date the course was taken and expiry date of the course.

          - Contractor to submit Manufacturer’s training and certification requirements and Contractor shall show full compliance to such requirements. Where re-certification is required for training courses, this shall be kept current and proof to be supplied that such re-certification took place within the time frame allowed. The Engineer shall make the assumption that this period will not exceed three years for cabling certification, and one year for software certification where applicable.

          - Contractor shall maintain an installation staff whose sole function is the installation of low voltage cabling and equipment and shall not utilize additional personnel obtained by means of a temporary placement or staffing agency.

          - Contractor shall not utilize apprentice or trainee personnel for the termination of low voltage cabling. Furthermore, apprentices or trainees may only assist in the pulling of low voltage cabling. The primary labourer for the pulling of low voltage cabling must be a certified installer.

          - The technicians responsible for pulling cable shall be monitored and supervised by the Contractors. Staff certified by the Manufacturer. The technicians responsible for the termination and testing of all cabling shall possess a current Installation and Maintenance certification by the Manufacturer. Details of the names of the Certified Termination staff shall be provided in writing with this bid together with valid copies of certificates and ID badges. ID badges of trained staff shall have a picture of the technician.

          - Manufacturer shall provide verification in writing that Contractors trained staff certifications are both valid and current.

          - Contractor’s installation staff shall consist of 50% Manufacturer certified installation personnel. The remaining shall be either apprentice installation personnel or labourers under full time employment by Contractor.

          - Preference shall be given to Contractor companies with BICSI trained and qualified RCDD, NTS, OSP, WD and ESS qualifications. They shall assist during the design stage of the project, and for the duration of the contract liaise with the Client Engineer on all aspects of the project.

          - Contractor shall have two dedicated RCDD’s assigned to the project as part of the design and project management team, who shall be the sole point of contact for the Engineer. The project manager shall provide regular project updates to the Engineer as to the percentage of job completed broken down by category of work. For example:- horizontal cabling,  backbone  copper backbone fiber, infrastructure pathways and spaces, the status of any unforeseen circumstances, and/or changes to the project design necessitated by field conditions.

          - Contractor shall have BICSI.ITS Technician qualified staff that shall supervise the installation and conduct all copper, fibre and in-building wireless cable tests. Such staff shall have undertaken BICSI.ITS Installer 1 and ITS Installer 2 training too.

        - Manufacturer Qualification

          - For the following items Contractors shall provide manufacturers written confirmation and documentary proof with their bid response, failure to adhere to this will lead to disqualification from the bid submission.

          - The Contractor shall have each Manufacturer, confirm in writing, compliance to the Manufacturers requirements within this document.

          - Contractors shall provide the Manufacturers original documentation in relation to the requirements.

          - All structured cabling system solutions requested shall be supplied and guaranteed by a single manufacturer.

          - The Manufacturer is to confirm in writing whether 3rd party Contractor manufacturers are utilized for their copper and fibre cable and products and/or software where applicable. Full details of such parties including location, manufacturing facility or facilities are to be supplied.

          - The Manufacturer shall confirm in writing, that they have a registered Business Address in the JOR Office Address, Office Size, and number of employees who are employed directly by the Manufacturer (Employees of the Manufacturers appointed agents or distributors will not be accepted). Confirmation is required that the Manufacturer’s JOR resident support staff have a minimum of 5-year experience in JOR or neighboring countries markets market and that a minimum of 2 RCDD certified –BICSI–technical support Staff work for the Manufacturer in the JOR Office. RCDD Staff names to be provided and verified electronically at https://www.bicsi.org/forms/Verify/CredentialHolder/.

          - The Manufacturer shall confirm in writing to have a minimum of ten (10) years’ experience in the manufacture of the specified cabling products and shall provide the ISO 9001/14000 Certificates.

          - The Manufacturer to confirm in writing, the year in which they introduced their complete 4connector, 100 meter Category 5, Category 5e, Category 6, Category 6A and OM3 Multimode/ OM4 Multimode and OS2 Single mode Solutions  (a  full  solution  is  defined  as  cordage,  cable,  outlets  and connecting hardware).

          - Manufacturer to provide details of how the Client’s investment in product will  be  protected  for  the  full  period  of  the  warranty.  Replacement parts and upgrade paths shall be detailed in full.

          - Manufacturer  to  provide  full  traceability  of  all  copper  and  optical  fibre cabling by printing unique serial number on the outer jacket of the cable Manufacturer must provide on-line tracking system to allow the client to reference the test values of the specific cable based on this unique serial number

          - Manufacturer to provide full details of their registered installer/ integrator/ contractor programme. Should there be differing levels or tiers of status, this should be clearly defined in terms of criteria to be met versus criteria met by the Contractor.

          - Manufacturer shall have a minimum of three  “Top  Tier”  qualified integrators/  Contractors  capable of projects in excess of  $1  million Furthermore,  such  integrators/  Contractors  shall  have  maintained  an unbroken contract with the Manufacturer for a minimum period of 3 years.

          - Manufacturer  shall  have  a  minimum  of  three  “Lower  Tier”  qualified  integrators/ contractors capable of projects up to $1 million  Furthermore, such integrators/ Contractors shall have maintained an unbroken contract with the Manufacturer for a minimum period of 3 years, and they shall be a prequalified Supplier.

          - Manufacturer  to  provide  details  of  its  logistical  capability,  including  the following:

            - Number of and location of manufacturing facilities globally

            - Number of and location of manufacturing facilities in the region

            - Number of and location of distribution facilities in the region

            - The value of Manufacturers’ products in distribution and warehouse facilities in the region, and the value of products held in warehouses that supply to JOR.

          - Manufacturer Environmental Policies and Compliance.

            - The Manufacturer shall confirm in writing to have a minimum of ten (10) years’ experience in the manufacture of the specified cabling products and shall provide the ISO 9001/14000 Certificates.

            - Manufacturer to provide compliance certification to ISO 14001-2004 and indicate how many of its manufacturing facilities comply on a global basis.

            - The European Union’s directive limits the levels of six hazardous materials including lead, cadmium, mercury, hexavalent chromium, polybrominated biphenyl (PBB) and polybrominated diphenyl ether (PBDE) flame retardants in electrical and electronic equipment. If the manufacturer has facilities in the EU, proof of compliance to be submitted.

            - Manufacturer  must  provide  compliance  certification  to  the  European Restriction  of  use  of  certain  Hazardous  Substances  (RoHS)  Directive, 2002/95/EC   Manufacturer  to  indicate  how  many  of  its  global manufacturing facilities are in full compliance with RoHS requirements.

            - If the Manufacturer has facilities in the United States, it is required to show how many of the US  facilities participate in the US  Department of Energy Voluntary Greenhouse Gas Reporting Climate Wise/Energy Star Program to reduce greenhouse gas emissions voluntarily.

            - The company shall provide evidence of its compliance to: The Registration, Evaluation, Authorization and restriction of Chemicals (REACH), Regulation (EC) No 1907/2006 or other national/international equivalent standard, directive or regulation.

            - As a large percentage of any installation utilizes cables and cable drums, Manufacturers are required to show what initiatives are in place to recycle cable boxes and drums.

            - In accordance with Owner’s green environmental policy, preference will be given to Manufacturers of cable products that are supplied in recyclable boxes or on recyclable wooden reels.

      - PRE-INSTALLATION MEETINGS

        - Comply with requirements of Division 01.

        - Convene minimum one week prior to commencing work of this section.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide (12) months full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of (1) year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Three Engineers. Training shall be sufficient enough to enable the Engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - HORIZONTAL CABLING

        - Horizontal cables shall be unshielded twisted pair cables for all IT networks except for data outlets where it should be shielded type. Horizontal data cable shall comply as minimum requirement to the Class E Standard defined by standard   ISO/IEC 11801 (Category 6 per TIA/ EIA-568.B.2). The cable shall meet the following min performance values:

          - CLASS E:

| Frequency MHZ | Attenuation | PS NEXT | PS ACR-N | PS ACR-F | Return Loss | Coupling attenuation | PS ANEXT | PS AACR-F | Propagation delay | Delay Skew | Unbalance Attenuation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MHZ | dB | dB | dB | dB | dB | dB | dB | dB | US | US | dB |
| 1 | 4.0 | 62.0 | 58.0 | 60.3 | 19.0 | NA | - | - | 0.580 | 0.050 | 40.0 |
| 4 | 4.2 | 60.5 | 56.4 | 48.2 | 19.0 | NA | - | - | 0.562 | 0.050 | 40.0 |
| 10 | 6.6 | 54.0 | 47.4 | 40.3 | 19.0 | NA | - | - | 0.555 | 0.050 | 38.0 |
| 16 | 8.3 | 50.6 | 42.3 | 36.2 | 18.0 | NA | - | - | 0.553 | 0.050 | 34.9 |
| 20 | 9.3 | 49.0 | 39.7 | 34.2 | 17.5 | NA | - | - | 0.552 | 0.050 | 33.5 |
| 31 | 11.7 | 45.8 | 34.1 | 30.4 | 16.5 | 50.2 | - | - | 0.550 | 0.050 | 30.5 |
| 62 | 16.8 | 40.6 | 23.8 | 24.4 | 14.1 | 44.2 | - | - | 0.549 | 0.050 | 24.5 |
| 100 | 21.7 | 37.1 | 15.4 | 20.3 | 12.0 | 40.0 | - | - | 0.548 | 0.050 | 20.3 |
| 125 | 24.5 | 35.4 | 10.9 | 18.3 | 11.0 | 38.1 | - | - | 0.547 | 0.050 | 18.4 |
| 155 | 27.6 | 33.8 | 6.2 | 16.5 | 10.1 | 36.2 | - | - | 0.547 | 0.050 | 16.5 |
| 175 | 29.5 | 32.9 | 3.4 | 15.4 | 9.6 | 35.1 | - | - | 0.547 | 0.050 | 15.4 |
| 200 | 31.7 | 31.9 | 0.1 | 14.2 | 9.0 | 34.0 | - | - | 0.547 | 0.050 | 14.3 |
| 250 | 35.9 | 30.2 | 5.8 | 12.3 | 8.0 | 32.0 | - | - | 0.546 | 0.050 | 12.3 |

        - The Class EA (Cat 6) cables shall have the following characteristics and minimum performance parameters at 20° C

| Characteristic impedance | 100 Ω ± 5%, 10-250MHz |
| --- | --- |
| Material | Tinned Copper, 23AWG |
| Drain wire | Tinned Copper |
| External Diameter | 8.5 mm |
| Operating temperature | 0 to 60 deg. C |
| Mutual capacitance (maximum) | 5.1 nF/100 m |
| Capacitance Unbalance Pair Ground Max. | 50 pF/100 m |
| Propagation Delay skew Max | 25ns/100m |

        - Color-Coding of the cable pairs shall be as follows:

| PAIRS | WIRE 1 | WIRE 2 |
| --- | --- | --- |
| 1 2 | White/blue White/orange | Blue orange |
| 3 4 | White/Green White/brown | Green brown |

        - Patch Cords – Copper

          - RJ45-RJ45 Cat 6 patch cords shall be supplied with the system, to facilitate configuration of data ports by the Supplier of “Computer Network Equipment”. The number of patch cords supplied with the system shall not be less than 40% of the total number of data ports included in the system. These shall be handed over to the Network equipment Supplier after testing and commissioning of the cabling network.

          - The patch cords shall be factory terminated with patch plugs that mate with the connecting block to provide gas-tight cross-connections. Patch cords shall be of 4-pairs with lengths varying from 1.5 to 2 m.  Longer lengths shall be made available if required for any specific location. In addition to providing end-user control of the system, patch cords shall reduce potential cross-talk & signal interference and should be considered over jumper wire when supporting high speed bit-rate applications. The patch cords shall be category 6A and employ cross-talk cancellation technique to provide superior near-end cross-talk (NEXT) performance.

          - Patch cords shall be designed to eliminate polarity reversals and split pairs, also to eliminate the need for tools and trained technical staff. Line moves and rearrangement can be made quickly an easily with the assurance of a quickly connection every time.

        - Telecom (IP Voice / Data) Outlets (TO)

          - The RJ45 connector shall be screened to ensure protection against EMI and for Alien cross -talk compliance. It offers the 500 MHz performance required to be used to form a 100 meters Class EA channel as specified in ISO/IEC 11801:2002/A1:2008 and EIA/TIA 568 B2-10.

          - Each connector shall provide T568B colour code identification for the pins at the rear of the connector. The punch down is to be in accordance with the T568B colour code. Reassignment of pairs is forbidden.

          - All conductors from the 4 pair cable are to be terminated on the respective contacts.

          - To avoid installation errors, the wire organizer of the snap-in connector must be identified by the same standard colour coding as the wires.

          - In the case of a 3 or 4 connector Channel with CP, a specific version of connector having IDC contact suitable to receive stranded cable shall be used, in combination with 6A F/STP Class E single ended patch cords.

        - All outlets are fitted with removal shutters, which can be replaced by colour-coded shutters       (Red, Green, Blue, Yellow) available from the manufacturer standard product range.

        - The presentation of the outlet shall provide for labeling and identification. A transparent window shall protect the labeling tag.

        - To ensure protection against EMI, all connectors have to be fully screened with 360° EMC protection.

      - BACKBONE CABLING

        - Data/ voice Backbone

        - Fiber Optics backbone cabling will link main IT cabinet with IT cabinets within each floor.

        - Optical Fiber cable

        - Enhanced multi-mode OM3 fibers are required for the transmission of high rate data signals and to avoid limitations due to bottlenecks in the longest building and campus backbone links.

        - Single Mode multi strand fiber cable shall be used for main telecom connection to infrastructure telecom network within OCEC development site.

        - Technical Data – Fiber Transmission

| Fiber type | #### OM1 | OM1 Enhanced | OM2 (G651) | OM2 Enhanced | #### OM3 | OM3 Enhanced | SM (G652) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Attenuation | @ 850 nm (dB/km) |  |  |  |  |  | @1310 nm |
| Typical | ≤ 3.0 | ≤ 3.0 | ≤ 2.6 | ≤ 2.6 | ≤ 2.6 | ≤ 2.6 | ≤ 0.35 |
| Max. | ≤ 3.5 | ≤ 3.5 | ≤ 3.2 | ≤ 3.2 | ≤ 3.2 | ≤ 3.2 | ≤ 0.42 |
| Attenuation | @ 1300 nm (dB/km) |  |  |  |  |  | @1550 nm |
| Typical | ≤ 0.8 | ≤ 0.8 | ≤ 0.8 | ≤ 0.8 | ≤ 0.8 | ≤ 0.8 | ≤ 0.22 |
| Max. | ≤ 1.5 | ≤ 1.5 | ≤ 1.3 | ≤ 1.3 | ≤ 1.3 | ≤ 1.3 | ≤ 0.28 |
| Application | Transmission max. distance @ 850 nm |  |  |  |  |  |  |
| Fast Ethernet | 300 m | 300 m | 300 m | 300 m | 300 m | 300 m | - |
| 1 Gigabit Ethernet | 275 m | 550 m | 550 m | 800 m | 800 m | 1100 m | - |
| 10 Gigabit Ethernet | 33 m | 50 m | 82 m | 125 m | 300 m | 450 m | - |
| Fibre Channel 1Gbps | 300 m | 500 m | 500 m | 750 m | 900 m | 1.000 m | - |
| Fibre Channel 2Gbps | 160 m | 200 m | 200 m | 400 m | 500 m | 600 m | - |
| Fibre Channel 4Gbps | 80 m | 100 m | 100 m | 210 m | 300 m | 330 m | - |
| Application | Transmission max. distance @ 1300 nm |  |  |  |  |  |  |
| Fast Ethernet | 2.000 m | 2.000 m | 2.000 m | 2.000 m | 2.000 m | 2.000 m | 2.000 m |
| Gigabit Ethernet | 550 m | 550 m | 550 m | 2.000 m | 550 m | 550 m | 10.000 m |
| 10 Gigabit Ethernet | - | - | - | - | - | - | 10.000 m |

        - Tight Buffered Indoor and light duty Outdoor waterproof OF cable:

        - This optical fiber cable shall be used for indoor home run back to patch panel routes in risers, horizontal applications and for outdoor duct applications where there is permanent water present i.e. flooded duct. This cable shall be selected where the required fiber count is from 2 to 24.

        - The cable shall be suitable for connector manufacturer field termination processes (LC connectors) and for OF pigtails splicing.

        - The cable shall be a dry construction i.e. with no gel content. The jacket material shall be waterproof LSZH with a minimum fire performance of IEC 332 part 3C.

        - Every fiber shall be 900µm diameter secondary coated each being a different colour or suitably identified for termination identification.

        - The cable strength member shall be glass yarn laid longitudinally between the fibres and the inside wall of the outer jacket. The cable shall be dielectric construction, i.e. with no metallic content.

          - FDDI: 100 Mbps

          - Ethernet

            - 10 base FL

            - 100 base FX

            - 1000 base SX

            - 1000 base LX

            - 10000 base SX (*)

          - Fiber Channel:

            - 266 Mbps

            - 1000 Mbps

          - ATM:

            - 155 Mbps

            - 622 Mbps

            - 1000Mbit

- (*): in accordance with IEEE 802.3 ae

        - Optical Fiber Telecom Outlets

          - The dimension of the Optical Fiber Telecom Outlet are 125 mm x 74 mm x 34 mm (H x W x D)

          - Standard LC snap-ins couplers shall be available to load the OF Telecom Outlet.

          - Direct Termination of the connectors (LC) on to the fibers as well as splicing of pigtails (LC) shall be possible.

          - The front plate of the OF Telecom Outlet shall be compatible with the following connector types:  LC.

          - The fully loaded Outlet shall support up to 2 fibers up to 4 fibers when working with LC.

          - The OF Telecom Outlet shall provide management for 50 cm of fibre per link after breaking the fibers out from the cable. The OF Telecom Outlet shall accommodate the aluminium splice protections as well as the heat-shrink ones.

          - In the OF Outlet, the fibers have to be wired in such a way that the dual OF channel polarity is maintained. Wiring of the fibers has to be done according to the guidelines provided by the manufacturer.

          - All Outlets are fitted with removal shutters, which can be replaced by colour shutters (red, green, blue, and yellow) available from the manufacturer standard product range.

          - The presentation of the outlet shall provide for labeling and identification. A transparent window shall protect the labeling tag.

        - Optical Fiber Patch Panel

          - Optical fiber Patch Panels shall be mounted in 19" frames of the cabinets. The patch panels shall be equipped with a mechanism that ensures the retention and support of incoming cables. The patch panel shall be designed with a sliding mechanism enabling front side installation and maintenance work to be carried out without having to remove the entire panel.

          - The patch panel shall provide facilities to recess the front connector plate deeper than the front of the 19" rails of the cabinet. This will provide sufficient bend radius for the patch cords once connected to the panel. This shall also prevent damage to the patch cords when the cabinet doors are closed.

          - Direct Termination of the connectors (LC) on to the fibers as well as splicing of pigtails.

          - The Patch Panel shall provide management for 1m of fiber per link after breaking the fibers out from the cable.

          - The front plate of the 12/24/48 ports modular Patch Panel shall be compatible with the following connector type LC.

          - Standard LC   couplers shall be available to load the modular patch panel.

          - The fully loaded panel (One height unit or 1HU) shall support up to 48 fibers when working with LC couplers.

          - Up to four optional splice trays should be supported to manage up to 48 splices.

          - In the panels, the fibers have to be wired in such a way that the dual OF channel polarity is maintained. Wiring of the fibers has to be done according to the guidelines provided by the manufacturer.

        - Optical Fiber Patch Cords

          - The Fiber snap-ins adapters will be connected to the active equipment by means of “Cross-over” duplex patch cords in order to maintain the duplex OF channel polarity.

          - The patch cords shall be available in lengths of 2 and 5 meters and have a LSHF-FR outer sheath.

          - The fiber patch cords shall be OM3.

        - Multimode connector performances:-

          - Maximum insertion loss at 850nm (IEC 61300-3-4): 0.5dB (LC)

          - Minimum return loss (IEC 61300-3-6): 40dB

          - Durability (IEC 61300-2-2): < 0.2dB

        - Compliance: LC connector compliant with IEC61754-20 specifications

      - FTTO Switch, Power supply, SFP Requirements

        - Standards ,- CE 2004/108/EC (EMC) and 2006/95/EG (Low voltage),- EN 60950-1:2006,- EN 55022:2006,- EN 55024:1998

        - High performance Layer 2+ Gigabit Ethernet Micro Switch

        - Full wire speed, non-blocking performance on all ports

        - Store-and-forward, 8192 MAC addresses, Jumbo Frames up to 10,240 Bytes, Manipulation safe, monolithic housing for high robustness, Tool-less snap in mounting due to 45x45 system.

        - One housing system ( high robustness and short installation times, improved electromagnetic immunity(EMC),no removable parts in mounted status, no removable parts in mounted status
safe against manipulation, Max. mounting depth 35 mm, Max. system height 59.7 mm.

        - Fixed integrated LED description , and chamfer edge at the bottom for simplified mounting

        - Integrated management agent based on a powerful ARM processor 800 MHz, powerful Linux operating system.

        - Full management functionality IPv4/IPv6, SNMPv1/2c/3, http/https, telnet/ssh.

        - Green IT Chip Technology Support Energy Efficient Ethernet IEEE Std. 802.3az

        - Storing of all events on storage media card.

        - Configuration of all ports via network management

- Port on/off
- Auto Negotiation (on/off)

- Speed (10/100/1000Mbps)

- Full-/half-Duplex, flow control

- Up to 256 VLANs (Access, Trunk, Hybrid)

- IGMP per VLAN

- Auto Crossover function (Auto MDI/MDI-X)

- Network Loop Protection

- Bandwidth management

- Data prioritisation (Class of Service)

- Port based prioritisation

- IEEE802.1q (VLAN-Tag)

- IP TOS-Field (DiffServ.)

- Prioritization scheme strict or weighted configurable

- overwriting of the incoming IEEE802.1q priority per VLAN configurable

- Authentication according to IEEE Std. 802.1X

- Via RADIUS server, 4 redundant server configurable

- VoIP security, separated authentication of the IP telephone

- Alternative: MAC authentication and limitation

- - Alternative: IEEE Std. 802.1X transparent, EAP-protocols are forwarded

        - Full auto negotiation functionality of the twisted pair ports for the detection of the speed 10/100/1000 Mbps, half/full-duplex and flow control

      - SFP Requirements

        - The SFP or “optical Transceiver” shall be compatible to the 45mmx45mm FTTO Micro Switch and shall be single mode fiber.

        - The SFP (Small Form Factor Pluggable) Transceiver must be usable  for data transmission up to Gigabit speed and have shall have a Single Mode 9/125 µm duplex, LC-connector.

        - The operating temperature shall be -40°C up to +85°C And shall supply a transmission distance of min. 10 km with a included digital diagnostic function.

      - FTTO Power supply Requirements

        - The switching power supply shall be provided for each for PoE+ Micro Switch with 65 W

        - The Dimensions shall not exceed for installation purpose: 128.5 mm x 44 mm x 30 mm (w x d x h).

        - Input voltage 90 - 264 VAC

- Input cable 3x 1.5mm2 open cable ends

- Output voltage: 54 VDC / 1.2 A, Full controlled and protected output

- Idle state protection: no minimum load required.

- CE: 2004/108/EC (EMC), 2006/95/EG (Low Voltage)

- Safety: EN60950 Emission

- The min. provided MTBF shall be 100.000 h (MIL-HDBK-217F)

- EXECUTION

      - INSTALLATION

        - Installation shall be by installers trained in the installation of Structured and extended performance data grade cable and equipment. Installing Contractor shall provide certificates of training for structured cabling as ISO/IEC for supervisors of installation personnel.  Certificates shall be acceptable from a manufacturer of the equipment listed or an independent training company.

        - All installing personnel shall be trained in the proper installation of extended performance data cable prior to installation by outside training course or in-house training program.  A letter describing training program shall be included in the shop drawing submittals.

        - All cables, outlets shall be installed in a neat professional manner:

          - Device plates shall be vertically plumb with edges flush to the wall and covering the outlet box.

          - Terminal block installation:  Blocks shall be vertically plumb and securely fastened to the back boards.  Station cables shall be routed in D-rings, brackets, and troughs and be securely fastened to prevent strain at the terminations.

          - Cable terminations shall comply with manufacturer’s installation instructions and industry guide lines.

          - Installer shall observe factory installation guidelines for pulling tension, bending radius, kinking, and proximity to lighting and other electrical equipment for all cables.

        - Cables shall be concealed within conduit or raceway below finished ceilings or in the floor trunk, and continuously below exposed structural ceilings as shown in drawings.

        - Cables routed above accessible ceilings and in utility areas shall be installed in cable trays, floor trunk and in conduits provided in the building.  Where cables leave the cable tray they shall be supported by bar joists or new tie wires in drop ceiling areas.  A buffer tie shall be installed on tie wires to minimize cutting or kinking of communications cables.

        - Cables not installed in cable tray, shall be supported along their entire length with cable support hooks.

        - All communications outlet boxes shall be finished with a cover plate, including outlets in modular furniture.  Blank plates shall be provided for all boxes that are not cabled at this time as indicated on the plans.

        - Fire Stopping: Fire stop all wall and floor/ceiling penetrations and pass through that they use to provide same time-rating as wall or floor/ceiling itself.

      - GROUNDING

        - Grounding system is provided by electrical work of the building project.

      - TESTING

        - General

          - All testing  shall  conform  to  the  latest  release  of  ANSI/TIA/EIA  568-C,  the manufacturer’s  warranty  criteria,  and  Engineer’s  acceptance  criteria Contractor shall be responsible to repair or replace any cable that does not meet Specification at no additional cost to the Project.

          - Contractor shall review every test report for accuracy, completeness and conformance to the Specifications.

          - After delivery of Materials to the Site, and prior to installation, all cables, cable reels and shipping cartons shall be visually inspected to detect possible damage incurred during the shipping and transport  Visibly damaged goods should  be  immediately  reported  to  the  vendor  and  returned  for replacement.

          - All test results are required to be documented and submitted in hard copy (summary only) and electronic (softcopy) format with the as-built documentation.

          - Contractor shall provide unaltered electronic test results submitted in the original software format of the respective test equipment manufacturer Text files or files that have been imported into a word processor or other text editor application shall not be acceptable.

          - Engineer retains the right to be present at any or all testing Contractor shall provide written notice 48 hours prior to the beginning of the testing process.

          - Independent 3rd party system testing may be required, at the discretion of Engineer  in  the  event  of  non-performance  of  the  specified  testing procedures,  submittals  and/or  installation  procedures   The  extent  and logistics of the independent testing shall be arranged by Engineer  All costs associated with the testing shall be the responsibility of the Contractor .

          - Engineer reserves the right to mandate re-termination or other reasonable rework  to  improve  the  performance  of  any  cabling  indicated  as  being  a “marginal pass”.

        - Fibre Optic Cable Pre-installation Test.

          - Contractor shall be responsible to pre-installation test all fibre optic cables Tests shall be performed while the cable is on the drum.

          - Contractor  shall  submit  a  test  plan  that  shall  include  procedure  and acceptance criteria for meeting this requirement.

          - Contractor shall replace the entire cable drum should any strand fail to meet the acceptance criteria replacing the cable shall not relieve Contractor of meeting project deadlines and milestones.

          - Contractor shall provide Engineer with written notification as to the results of the pre-installation testing within five (5) business days of completing the tests.

        - Optical Power Test

          - All fibre optic cables (backbone and horizontal) shall be tested to verify the optical loss performance.

          - Contractor shall perform optical power tests in both directions for each level of the backbone fibre optic cable (MC to MC, MC to IC and MC/IC to HC).

          - Each multimode fibre strand shall be tested at 850nm and 1300nm.

          - Each single mode fibre strand shall be tested at 1310nm and 1550nm.

          - All optical power meter tests shall be performed using a stable light source.

          - Contractor shall use the test equipment manufacturer’s standard form.

          - Test data shall include the following information:

            - Project

            - Origination Bldg /TR

            - Destination Bldg /TR

            - Cable Manufacturer

            - Cable Part Number

            - Cable Type (e g, Multimode or Single mode)

            - Cable Construction (e g, Tight Buffered, Loose Tube or Ribbon)

            - Jacket Rating (e g, OFNR, OFNP, LSZH, OSP, etc)

            - Connector Type

            - Transmit Level

            - Wavelength

            - Origin Panel/Port Number

            - Destination Panel/Port Number

            - Strand Colour

            - Receive Level

            - Link Loss

            - Date

            - Time

            - Temperature

            - Witness

          - The total allowable link loss shall be based on the calculations shown below For calculation purposes, a cable segment is based on an individual strand of multimode or single mode fibre strand terminated on each end with a fibre connector, excluding patch cables These calculations shall be used as the acceptance Criteria for the backbone cable.

        - OTDR

          - Contractor shall perform OTDR (Optical Time Domain Reflectometer) testing in the outbound direction only for each level of the backbone fibre optic cable (MC to MC, MC to IC, and MC/IC to HC).

          - The purpose of the OTDR tests shall verify the length of each strand, and the optical  integrity  of  each  fibre  (e g ,  opens,  terminations,  loss/km,  micro- ends, etc ).

          - Contractor shall ensure that the launch cable used during the OTDR tests conforms to the OTDR manufacturer’s specifications.

          - Contractor  shall  also  ensure  that  the  refractive  index  parameter  is  set  to equal that of the fibre manufacturer’s specifications.

          - All results shall be documented and provided in Contractor’s standard format

        - Return Loss (Reflectance) Test.

          - Contractor shall perform return loss (reflectance) tests on each single mode fibre strand in both directions for each level of backbone fibre optic cable (MC to MC, MC to IC and MC/IC to HC).

          - The minimum acceptable return loss (reflectance) shall be -58dB.

          - Any single mode cable/connector assemble failing to meet the acceptance criteria shall be repaired or replaced by the Contractor at no additional cost to the Project.

        - UTP/SFTP Cable Tests

          - Upon completion of UTP/SFTP cable installation, Contractor shall perform complete certification tests on every cable.

          - Testing shall be performed to published standards, including but not limited to, the latest revisions of EIA/TIA 568, ISO/IEC 11802 and all other applicable standards at the time of installation.

          - All  tests  shall  be  performed  with  a  certified  Level  IIIe  UTP/SFTP  test  device Certified  test  equipment  as  manufactured  by  Fluke  or  Agilent  shall  be acceptable  Contractor shall utilize the latest model/software revision for all testing  Engineer shall approve the use of alternate test equipment  All costs associated with calibrating test units shall be Contractor’s responsibility.

          - All UTP/ SFTP field testers shall be factory calibrated every twelve months by the respective manufacturer.   The calibration certificate shall be  provided to Engineer for review prior to the start of testing.

          - New test leads and/or calibration of testing instruments shall be provided at the beginning of each project.

          - For  any  given  project,  the  Contractor  must  use  the  same  test  equipment (manufacturer  and  model)  for  all  UTP/SFTP  cable  tests   Mixing  of  different manufacturer’s test equipment shall not be permitted.

          - All  test  equipment  shall  be  operating  under  the  latest  version  of firmware/software  as  provided  by  the  manufacturer   Contractor  shall  be responsible for all costs associated with test equipment firmware/software upgrades.

          - Prior to testing, Contractor shall perform the following setup procedures on the test equipment.

          - Enter all relevant project data into the test equipment, including technician/operator  name,  date  of  test,  project  name,  building,  floor,  TO number and jack position number, etc.

          - Enter appropriate cable manufacturer, manufacturer’s model number and electrical parameters of the cable, including nominal velocity of propagation.

          - Calibrate the scanner to the injector.

          - Setup the test equipment to fully test for all of the parameters listed below.

          - A  Permanent  Link  test,  as  described  in  the  ANSI/TIA/EIA  568-C  standards (including  most  recent  additions  and  addendum)  is  required  for  all  UTP/SFTP testing  at  a  minimum,  each  UTP/SFTP  cable  shall  be  tested  for  the  following parameters:

            - Pair-to-Pair NEXT (Near End Cross Talk)

            - Power Sum NEXT

            - Pair-to-Pair ELFEXT (Equal Level Far End Cross Talk)

            - Power Sum ELFEXT

            - Attenuation (Insertion Loss)

            - Return Loss

            - Propagation/Delay Skew

            - Cable length

            - Wire map

          - Contractor  shall  verify  that  the  TO  number  matches  the  number  on  the VP360 wiring block or patch panel.

          - Contractor shall troubleshoot and correct, repair or replace each cable that does not meet Specification.

          - A test result marked with an “*” will not be accepted.

          - A test summary and each individual UTP/ SFTP cable test shall be included as part of  Contractor’s  as-built  documentation  submittal   Only  the  Test  Summary Sheet shall be printed, and submitted in hardcopy format  The individual UTP/SFTP cable tests shall be submitted in electronic format only.

          - The Test Summary Sheet for each Telecommunications Room shall be signed and dated by Contractor’s Project Manager Contractor shall submit all cabletest results in electronic form on compact disk (CDROM) or digital versatile disc (DVD).

          - The electronic test results must be submitted in the original software format of the respective test equipment manufacturer Text files or files that have been imported into a word processor will not be accepted.

      - CUSTOMER INSTRUCTION

        - Provide instruction and training to Owner’s personnel for the following:

          - Labeling system and cross reference to documentation.  Provide 1/2 hour.

          - Interpretation of cable test results. Provide 2 hours

          - Operation of the cable management software:  Provide 2 hours

      - DOCUMENTATION

        - General

          - Contractor  shall  submit  to  Engineer  as  a  condition  of  final  payment  and acceptance all as-built documentation as required in these Specifications.

          - All documentation shall be submitted within 10 business days of completion of all Work.

          - All  documentation  shall  be  submitted  in  soft  copy  format  on  CD  or  DVD readable in MS-Windows 2000/XP.

          - Contractor is required to submit all as-built documentation in person and review it with Employer and Engineer during the Project Closeout Meeting.

        - Low Voltage Cabling System Documentation: Documentation requirements for the Low Voltage Cabling System shall include the following information Contractor shall electronically organize the documentation into folders for each section as follows:

          - CD/DVD label shall be entitled “Low Voltage Cabling System Documentation” and shall include the project name and date of submittal.

          - Backbone & Horizontal Fibre Test Results

            - Backbone Fibre - Summary of testing and Power Meter Test Sheets

            - Backbone Fibre – Summary of testing and OTDR Traces

            - Horizontal Fibre – Summary of testing and Power Meter Test Sheet

            - Horizontal Fibre – Summary of testing and OTDR Traces

          - UTP/ SFTP Horizontal Cable Tests

            - Summary

            - Individual Cable Detail Sheets

          - ID Charts

            - Backbone Fibre Strand ID Charts

            - Horizontal Fibre Strand ID Charts

            - UTP/ SFTP Wiring Block ID Charts or Patch Panel Charts

          - Record Drawings

            - Floor Plans showing TO locations and their respective faceplate number

            - All Telecommunications Room and Rack Layout Drawings

            - All schematic detail drawings

          - Manufacturer’s Specifications and Project Specific Warranties (Hard copies area acceptable when furnished by manufacturer).

        - Record Drawings

          - Contractor shall modify the design drawings to reflect all conditions of the low  voltage  cabling  systems,  including  but  not  limited  to  backbone  and horizontal  cabling,  TO  numbers, cable  tray  locations,  floor  core  locations, wall sleeve locations, equipment rack and wallboard layouts, etc.

          - Contractor  shall  provide  3  sets  of  soft  copies  of  all  as-built  drawings  in AutoCAD format ( dwg) on CD/DVD  Along with the soft copies, Contractor shall provide two hard copy sets of as-built drawings  Each hard copy set shall include (1) “A2” size and (1) “A0” size set of drawings.

          - Contractor shall add all revision information in the appropriate title block space all drafting will be two-dimensional and scaled as appropriate and clearly perceptible.

          - Contractor shall be responsible to obtain all of the electronic AutoCAD files from the Engineer Contractor shall be responsible for all costs associated with obtaining the files.

          - “X  References”  or  XREF  clipping  will  not  be  used   Match  Lines  will  be provided detailing the adjacent drawing number as required  Details or other drawing entities will be provided as blocks rather than bound to the drawing file.

          - All  text  fonts  will  be  the  original  typeface  and  sized  for  clarity  (notes, dimensions, etc ) to help distinguish annotations for the drawing  Text sizing will be dependent on drawing scales, but will be consistent throughout the individual site.

        - Fibre Strand ID Charts

          - A separate fibre strand ID chart shall be generated for each backbone and horizontal closet connector housing in the MC, IC and HC.

          - Contractor shall follow the same format as the strand ID charts provided in each closet connector housing and as shown elsewhere in the Specifications.

          - Contractor shall provide a copy of these charts electronically in either MS Word or MS Excel format.

        - UTP/SFTP - Patch Panel ID Chart

          - A separate UTP patch panel ID chart shall be generated for each patch panel The chart shall represent the physical layout of the patch panels and will identify the TO number, cable length, and the cable’s destination

          - General data such as Project Name, Date of Installation and Telecommunications  Room Location/Designation  shall  be  included  on  the chart  Unused ports on the chart shall be left blank for future use .

          - Contractor shall provide a copy of these charts electronically in either MS Word or MS Excel format.

        - Test Results

          - Contractor shall provide detailed test documentation on all of the required testing  Test Results shall include the following:

            - All fibre optic cable test results

            - Horizontal UTP/ SFTP test results

          - Horizontal UTP/ SFTP cable test results shall be documented, and shall include the following general information:

            - Contractor’s Company Name

            - Project Name

            - Date of Testing

            - Time (optional)

            - Telecommunications Outlet & Cable Number

            - Test Technician or Operator

            - Test Equipment Model/Serial No

            - Test Acceptance Criteria

            - Test Frequencies

          - Contractor  shall  provide  a  copy  of  the  horizontal  UTP/ SFTP  test  results electronically  in  the  original  software  format  of  the  respective  test equipment manufacturer.

        - Manufacturer’s Specifications

          - Contractor shall provide all cable and associated hardware manufacturer’s specifications, operational manuals, and warranties as normally provided by the manufacturer.

- END OF SECTION