- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Factory assembled main or sub-main LV Power Distribution Boards and accessories.

      - REFERENCES

        - The installation shall comply with the following standards, including all amendment.

          - IEC 61439: Low voltage switchgears and control gears (Part-1&2) assemblies (EN 60439-1 & 61439-1)

          - IEC 60529: Degree of protection provided by enclosures (IP Code).

          - IEC 60269: (Part Specification for Cartridge Fuses for voltage up to 1 to 4), BS 88 and including 1000V ac. and 1500V dc.

          - IEC 60255: Measuring Relays & Protection equipments, Elec. Relays

          - BS 1361: Specification for Cartridge Fuses for A.C circuit in Domestic and similar Premises.

          - IEC 60898: Circuit breakers for over current protection for household and similar installation.

          - IEC 61008 (Part-1 & 2):  Residual Current Operated Circuit breakers without integral over current protection (RCCB).

          - IEC 61009 (Part-1 & 2): Residual current operated circuit breakers with integral over current protection (RCBO).

          - IEC 60947-1: LV Switchgear & Control Gear- General rules.

          - BS 7626: Current transformers.

          - IEC 60947-1: Low voltage switchgear and control gear- general rule.

          - IEC 60947-2: Low voltage switchgear and Control Gear.

          - IEC 60947-5: (1	Control Circuit Devices and Switching Elements to 9 parts)

          - IEC 60947-3: Switches, Disconnector Switch & Fuse Combination Un

          - IEC 60947-4: (1 Contactors and motor starters to 3 parts)

          - IEC 60947- 6 (1 to 2 parts): Multiple function equipment -Transfer Switching, Control & protective switching devices

          - IEC 60947- 7 (1 to 3 parts): Ancillary Equipments – terminal Blocks for Copper conductors & safety requirements for Fuse TB

          - BS 5472: Spec for low voltage switchgear and control gear for Industrial Use Terminal

          - Making & Distinctive Number. General Rules.

          - BS 159:	Busbars and busbar connections

          - BS 5685 / IEC 60051: Electric Meters

          - Public Authority for Electricity and Water Requirements

          - Notes mentioned on the Tender drawings

          - Local Codes, Standards and Regulations.

      - SUBMITTALS

        - Submit manufacturer's catalogs and data including schematic drawings, dimensioned layout of equipment and accessories, technical specifications, installation instruction and general recommendations. Include data substantiating that the proposed units comply with the project requirements.

        - Submit dimensioned outline drawings of each distribution board/switchboard showing all leading dimensions and the estimated weight of the equipment.

        - Submit fully detailed dimensional drawings for metering panels and main low voltage panels approved, signed and stamped from local power utility / electrical power service provider.

        - The contractor shall provide these approved drawings before any panel being manufactured, otherwise if any panel rejected by the local power authority/ Engineer the contractor shall re-supply/ install new approved one at his own cost.

        - Submit fully detailed dimensional drawings for all electrical rooms/ substations with sections and elevations, connections details, cable/ trays/ busways’ routes and suspension details, natural/ mechanical ventilation,  ..etc. and any details requested by the Engineer.

        - Submit manufacturer's fabrication, builders work and installation drawings showing all significant details of each main and sub-main LV Power Distribution Boards/switchboard including the following:

          - All components.

          - Fuse, circuit-breaker and switch ratings.

          - Current and voltage transformer ratios, class, terminal markings and output.

          - Instruments, including scale details.

          - Relay types and characteristics.

          - Indicating lamps, including color.

          - Position of switches, and details of function.

          - All internal connections, with terminal markings.

          - Arrangement of terminal blocks.

          - Wire numbers.

          - Size, type and color of secondary wiring.

          - Principal physical dimensions, including clearances required for removing covers, opening doors, operating handles, withdrawing equipment, etc.

          - Position of all panel face equipment.

          - Identification of all equipment, and appropriate label inscriptions.

          - Foundation details, including weights and fixing points.

          - Cable entry details including gland and gland plate provisions.

        - Submit list of tools, test equipment, spare parts and ancillary equipment.

        - Provide samples of all proposed devices, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Submit the factory test reports verifying that the LV Power Distribution Boards have successfully passed all routine tests. Type tests results shall be submitted, when required by the Engineer.

        - Method Statement of installation, connection, adjustments, calibration, setting, testing, operation and commissioning for each proposed panel and all devices enclosed within.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations, configurations, and ratings of switchboards and their components on single line diagrams and plan layouts.

        - Operation and Maintenance Data: Submit spare parts data listing; source and current prices of replacement parts and supplies; and recommended maintenance procedures and intervals.

      - QUALIFICATIONS

        - Manufacturer: Firms regularly engaged in manufacture of the main or sub-main distribution boards of types, sizes and ratings required, whose products have been in satisfactory use in similar service for not less than 10 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - QUALITY ASSURANCE

        - The distribution boards shall comply with the requirements of BS, IEC and Local Standards.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver, store, protect and handle products to site under provision of Section 01 60 00 – Product Requirements.

        - Deliver in 1 .2m maximum width shipping splits, individually wrapped for protection and mounted on shipping skids.

        - Accept switchboards on site. Inspect for damage.

        - Store in a clear, dry space. Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect units from dirt, water, construction debris and traffic.

        - Handle in accordance with manufacturer’s written instructions. Lift only with lugs provided for the purpose. Handle carefully to avoid damage to switchboard internal components, enclosure and finish.

      - ENVIRONMENTAL REQUIREMENTS

        - Conform to service conditions specified in Section 26 05 00 during and after installation of switchboards.

      - FIELD MEASUREMENTS

        - Verify that field measurements are as indicated on approved shop drawings.

      - MAINTENANCE MATERIALS

        - Provide maintenance materials under provisions of Section 01 92 00 – Closeout Procedures.

        - Provide two of each key and any special tools required for operating or removing the breakers.

      - SPARE PARTS

        - Provide 5 % of each size and type of fuse installed but no less than five of each.

        - Provide 5 % of lamps of each LT panel, switchboard, distribution board, lighting control panels but no less than five of each.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - All materials used in the manufacture and installation of the LV power distribution boards shall be of high quality and of proven suitability for the functions they will perform and the conditions they will meet in service.

        - For remote monitoring/controls, comply with the requirements as given in Section 25 50 00.

        - Allow for witness tests to be carried out in factory and give at least 14 days notice before the tests are to be carried out.

        - All LV distribution boards shall be of the same brand and of similar brand as that of panelboards

        - All circuit breakers shall be of the same brand.

      - LV POWER DISTRIBUTION BOARDS /MDB

        - LV power distribution boards/switchboards shall be designed and constructed to withstand for one second without damage, thermal and mechanical stresses which might arise under short circuit conditions up to the prospective busbar short circuit current. Power distribution boards shall be in compliance with IEC 439-1.

        - Main L.V. panels shall be of the floor mounting front access, cubicle pattern type,              comprising main incomer of air circuit breakers and fixed outgoing (M.C.C.B's) and bus bars.  Main L.V. panels shall comply with form 2 of BS EN 60439-1994.

        - Main LV panels shall withstand short circuit current 65KA for 1 second.

        - Switchboards shall provide a degree of protection against contact with live or moving parts, and against the entry of solid foreign bodies and liquid, to IP 32 standard in accordance with the definitions contained in relevant standards.

        - Switchboards shall be self-contained, free-standing, floor mounting, flush-fronted, multi-cubicle Class 3 or multi-box type as called for on the Drawings and shall be constructed in sections where necessary to facilitate transport and erection.

        - The overall height of each switchboard shall not exceed two meters unless otherwise shown on the Drawings.

        - Each switchboard shall be designed for front access and top or bottom entry as shown on the Drawings. Cable terminations and space for terminations shall be suitable for the sizes of cable. All switchboards shall be capable of extension at both ends and busbar chambers shall be fitted with removable end covers.

        - Individual cubicles from which cubicle type switchboards are built shall be rigidly constructed from folded steel panels (not less than 1.5mm thick), and sections firmly welded together, and the required number of cubicles shall be bolted or welded together. Switchboards constructed from flat steel plates on a framework of rolled steel angle shall not be accepted. All switchboards shall be provided with adequate lifting eyes, which shall be removed after the boards are in place, and replaced by screw-in plugs. When a switchboard is sectionalized for assembly on site, the sections shall be provided with adequate means of locating adjacent sections to ensure accurate alignment.

        - Each switchboard shall be supplied with removable undrilled steel plates for cable glands and conduit entry. Where single core cables are used the gland plates shall be brass or non-conducting.  All conduits, trunking and cables as shown on the Drawings, shall be accurately located and drilled, cut and threaded on site.

        - LV switchboards shall be enclosed with lockable doors. All "live" metal shall be insulated and the operator shall not be able to accidentally come into contact with "live" connections or busbars when energized. All cable terminations shall be fully shrouded and shall permit connections to be made with adjacent circuits live.

        - All equipment mounted in switchboards shall be fully accessible for maintenance. Switchboard compartments shall be fitted with hinged doors, neoprene or foam rubber gasketed, and doors shall be provided with lever type locking handles having integral cylinder locks.  All locks shall be operable with a common key, the number of keys supplied being two per lock up to a maximum of 10 per switchboard.

        - Molded case circuit breakers in switchboards shall comply with IEC 947-2. Switches, fuse-switches, switch disconnectors and disconnectors shall comply with Section 26 27 26 and BS and IEC requirements.

        - Motor starters installed within the Power Distribution Boards shall comply with the requirements given in Section 26 29 16.

        - All disconnectors, switch disconnectors, switches and circuit-breakers shall be provided with the means to enable them to be locked in the “off” position.  When used as earthing switches they shall be capable of being locked “on” when closed to the earth connection.

        - Busbars shall be four-pole, air insulated of uniform cross-section throughout their length, with a continuous current rating not less than that shown on the Drawings and shall be arranged horizontally and vertically through each switchboard. Current ratings shall take account of reduction in section caused by drilling for connections and supports.

        - Busbars and the connections from them to the various items of switchgear shall be manufactured from hard drawn high conductivity copper.

        - Busbars shall be supported on non-hygroscopic, non-tracking insulators of sufficient strength to withstand, without damage, the forces set up, either by thermal effects during normal operation or by electromagnetic effects under short circuit fault conditions.

        - Busbars shall be housed in separate compartments, which shall not contain any wiring or apparatus other than that for connecting to the busbars.

        - Access to busbars and busbar connections shall be possible only after the removal of covers secured by bolts or studs.  Such covers shall be identified externally by “Formica” engraving laminate labels bearing the inscription “BUSBARS” in black lettering not less than 10 mm high, on a white background.

        - The cross-sectional area of the neutral busbar shall equal that of a phase bar.

        - Each cubicle or box section shall be provided with sufficient busbar links to enable cubicle sections to be easily joined.  Facilities shall also be provided for extending the busbars to extra cubicle sections, if required, at some later date.

        - Metering current transformers shall be installed on the incoming side.

        - The equipment for each outgoing circuit shall be housed in a separate compartment so that it can be maintained without risk of contact with live connections on another circuit.

        - Supplies for control circuits shall be taken from within the compartment of the related item of switchgear, and a fuse unit fitted with a separate protective device shall be fixed within the compartment to protect the control circuit.  Where control circuits pass through auxiliary contacts the protective device shall also be the means of isolation for the terminals of these contacts.

        - Where auxiliary contacts are used for interlocking purposes and supplies are derived from other sources, isolating facilities shall be provided to ensure that the auxiliary contacts can be made safe.  The isolating facility shall be in the form of an auxiliary switch on the respective compartment isolating device or a separate isolator mounted within the respective compartment.  Where a separate isolator is provided a clear warning notice made from “Formica” engraving laminate shall be fixed by screws in a prominent position in the compartment stating “WARNING - ISOLATOR AUXILIARY CONTACTS”.

        - Where the external cables to or from the switchboard are shown on the Drawings as being PVC or XLPE insulated twin and multi-core cables, armoured or unarmoured, the appropriate units of the switchboard shall be supplied with suitable brass compression glands of the correct sizes.

        - Compression glands for PVC insulated and sheathed twin and multi-core cables shall comply with the requirements given elsewhere in these specifications.  All component parts of a cable gland shall be of the same manufacture.

        - All internal connections and small wiring shall be carried out using PVC insulated cables complying with BS requirements and all terminals shall be marked in accordance with BS standards.

        - All small wiring shall be neatly bunched and cleated in harness form, using purpose-made plastic cable ties, or shall be enclosed in purpose-made plastic small wiring trunking.  Wiring cleated to metal surfaces shall be spaced off the metal or otherwise insulated from it.  Metallic “buckle clips' shall not be used for internal wiring.  Wiring to swing doors or other moveable items shall be flexible cables neatly bunched and constrained by a flexible harness.

        - Small wiring to which external connections have to be made shall be terminated on approved type terminal boards which shall be easily accessible and conveniently arranged to facilitate the connection of incoming and outgoing multi-core cables. Each terminal unit shall have separate incoming and outgoing terminals and no more than one wire shall be connected to any one terminal unless the terminal is specifically designed to take more than one. Each terminal board for external wiring shall have at least 10% spare capacity with a minimum of two spare terminals. All terminal boards shall be numbered in sequence to match the numbering on the wiring or connection diagrams.

        - All spare contacts on relays, contactors, and the like shall be wired to easily accessible terminal blocks, as above, suitably positioned for future external wiring.

        - Main earthing terminal shall consist of a copper earth bar sized in accordance with BS for the prospective short-circuit current.  The earth bar shall be unjointed except between cubicle sections and shall extend through the length of the switchboard.  The earth bar shall be connected to the earthing conductor via an external test link.  Minimum earth bar size shall be 25 x 3 mm. Each cubicle and all protective conductors shall be bonded to the earth bar.

        - A bonding conductor shall connect the earth bar to each gland and/or armour clamp where cables terminate at the switchgear. All equipment which is not specifically earthed separately shall be bonded to the main earth bar.

        - Each switchboard shall be equipped with the instruments, meters, Polyphase meters and associated apparatus as shown on the Drawings. All instruments, meters and associated apparatus shall comply with the detailed requirements set out elsewhere in this specification under the heading Instruments and Metering.

        - Each incoming and outgoing circuit on the switchboard shall be clearly identified on the front panel by means of an engraved label bearing, in black letters on a white background. The labels shall be of plastic engraving laminate with lettering not less than 5 mm high and shall be secured to the panel front with instrument headed machine screws.  Where rear access is available labels shall also be fixed to the rear panels.

        - Warning labels shall be fitted in all places where the removal of covers or access panels may expose live equipment operating at a pressure exceeding 250 V between phases or to earth. Warning labels shall be of plastic engraving laminate with red lettering on a white background, and shall bear the inscription “DANGER - LIVE PARTS OVER 250 V” in letters not less than 10 mm high.

        - All equipment and apparatus, both inside and outside the switchboard, including instruments, meters, and relays, which is not clearly identified by integral labeling, shall be adequately labeled in the manner described above for front-of-panel circuit labels.

        - All fuse-switches, switch-fuses, miniature and molded case circuit-breakers, disconnectors, switch-disconnectors and distribution boards forming part of low voltage switchboards shall comply with the requirements set out in Sections  26 27 26 and 26 28 23.

        - No switch, breaker or fuse gear in switchboards will be accepted unless it has type test certification to the requirements of the relevant standard from an independent testing authority.

        - A high voltage pressure test shall be carried out with all isolators closed and power fuses fitted but having all control circuits disconnected.  The panels shall withstand for one minute a voltage of 2 kV across the following points:

          - Phase to phase.

          - Phase to neutral.

          - Phase to earth.

          - Neutral to earth.

        - Works tests on busbars in accordance with the requirements for routine tests shall be included.

        - Approval of tests and test certificates that may be given shall not relieve the Sub-contractor of the obligation to supply the complete equipment in accordance with the requirements of the Specification, Schedules and Drawings.

        - Where designated, the emergency power supply connection shall be an automatic source changeover with the mechanical and electrical interlocking.

        - Anti-Condensation Protection

          - Switchboards shall be provided with thermostatically controlled, anti-condensation heaters protection using suitably rated space heaters suitable for 230V, 50Hz, 1ph supply.

          - Power supply to the space heater shall be provided from internal source at one point. Further distribution including necessary MCB’s for incomer and distribution shall be provided by the contractor if deemed necessary at no further cost.

          - Unless otherwise specified. Anti-condensation heaters shall be arranged to provide uniform heating of the panel and shall maintain the panel interior at approximately 5 °C above ambient temperature, using thermostat controls.

          - The heater elements shall be protected against accidental touching by personnel performing tasks in the control panel.

          - Anti-condensation heaters shall also be provided in the cable compartments.

      - ACCESSORIES

        - The room for main LV power distribution board/switchboard shall be complete with all accessories necessary to form a complete installation including, but not limited to, the following operating and safety accessories:

          - One (1) pair of insulating gloves.

          - One (1) rubber mat 10 mm thick x 1000 mm wide and extending the full length of the equipment.

          - One (1) notice and safety instruction chart including first aid chart for electric shock.

          - One (1) set of spare control circuit fuses.

          - Any other equipment necessary to comply with the standards and maintenance/safety requirements.

      - SUB-MAIN DISTRIBUTION BOARDS (SMDBS)

        - Sub-main distribution boards (SMDBs) shall be installed in floor areas as shown on Drawings. They shall be floor or wall mounted cubicle type containing incoming & outgoing fixed type M.C.C.B's. Enclosure to min IP32. The boards shall be capable of withstanding without damage a fault level as shown on Drawing at 400volts.

        - All M.C.C.B.'s shall be fixed type in all boards and shall be provided and installed as part of this Contract.

        - SMDB shall be manufactured by a specialist manufacturer as detailed in the Schedule for cable entry from above and below.

        - SMDBs shall be of 600V/1000V insulation grade and shall be designed, fabricated and assembled in compliance with form 2 of BS EN 60439-1:1994 and shall be suitable for the operation of 400/230V, 50HZ supply systems.

        - Panel casing shall be fabricated using a minimum of 2mm. thick corrosion resistant galvanized steel sheets or corrosion resistant steel sheets coated with the alloy of aluminum, zinc and silicone (ALUZINK).

        - Boards shall also be air tight, fully interlocked and factory fabricated with degree of protection min. IP32.

        - SMDBs shall contain a suitable earth bar to which all items of equipment and cable glands are bonded. The minimum size of this earth bar shall be as per IEE Regulations. Similarly neutral bar shall be provided of the same cross section as live bars.

        - SMDBs shall be constructed to conform to the specified requirements of the local codes, relevant British Standard and Codes of Practice. The drawings of proposed arrangements shall be forwarded to the Engineer for approval prior to commencement of manufacture.

        - The contractor shall be responsible for checking access, builder work, to ensure that the panel is constructed and installed as required by the Local Requirement Regulations, Relevant British Standards and Code of Practice.

        - The rated service short-circuit breaking capacity of all outgoing & incoming MCCB’s in SMDBs shall be the same as that for SMDB busbar short circuit current rating as indicated on drawings.

        - All bus bars section in the Panel shall be designed to withstand the max. fault level capacity as indicated on Drawings.

        - MDBs & SMDBs shall be equipped with the instruments, digital Polyphase meters and associated apparatus. All instruments, meters and associated apparatus shall comply with the detailed requirements set out elsewhere in this specification under the heading Instruments and Metering.

        - MDBs & SMDBs shall be equipped with surge protection devices.

- EXECUTION

      - INSPECTION

        - The Contractor shall examine the rooms, areas and conditions under which the main or sub-main LV power distribution boards/switchboards are to be installed, and correct any unsatisfactory conditions detrimental to the proper and timely completion of the work. Do not proceed with the work until unsatisfactory conditions have been corrected in a manner acceptable to the Engineer.

        - Agree with the manufacturer of the switchboards, the suitability of the Civil Works for foundations which must be compatible with equipment and all sizes and details must be checked and confirmed before concrete is poured, or revised with the approval of the Engineer where necessary. It is the Contractor's sole responsibility to supply all materials and to construct in the correct location, level and true grade, the concrete base, and to connect all incoming and outgoing cables.

      - INSTALLATION

        - Installation of LV power distribution boards/switchboards shall be in accordance with manufacturer's written instructions and shall comply fully with the requirements of BS, IEC, Local Standards/ Regulations and recognized industry practices.

        - Install the switchboards on to bases using appropriate lifting equipment to ensure that no damage occurs. When correctly located, the unit shall be anchored in position and tested before and after connecting the incoming and outgoing cables.

        - Supply all material for construction of base in correct location, level and time grade and for connection of all incoming and outgoing cables.

        - Check ratings of all circuit protection devices and fill out the circuit directory card upon completion of installation work.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - Prior to energization of main and sub-main LV power distribution boards/switchboards, following tests shall be carried out:

          - Testing of all accessible bolted connections to manufacturer’s torque specifications.

          - Testing of insulation resistance.

          - Testing of electrical continuity / short circuits of the circuits.

          - Current injection testing of all circuit breakers and protective devices.

          - Ratio tests of all current transformers.

        - Subsequent to wire and cable hook-ups, energize the LV power distribution boards and demonstrate functioning in accordance with the requirements. Check whether all outgoings are connected as per load schedules. Record changes in the schedule for final as-built, if acceptable to the Engineer.

      - ADJUSTMENTS

        - Adjust circuit breakers, protective relays and other control devices to provide adequate over current protection and selective tripping with downstream devices in accordance with short circuit and protection coordination study and after proper coordination with protection settings of Electricity Supply Authority.

      - FACTORY TESTING

        - All factory tests shall be performed at manufacturing locations in the presence of minimum three persons one each from client, project / construction manager and consultant. Contractor shall make provision for all the expenses of business class air travels, insurance, five-star hotel accommodation, local travel etc. to witness these tests.

- END OF SECTION