- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Electrical identification to identify all electrical items for easy operation and maintenance including, but not limited to the following:

            - Nameplates and labels.

            - Wire markers.

            - Colour coding of raceways.

            - Circuit identification charts.

            - Cable identification tags.

            - Cable warning tapes.

            - Cable markers.

            - Equipment warning/danger signs.

      - REFERENCES

        - IEC 364	 Electrical Installations

        - BS 7671 Electrical Wiring Regulation (IEE 17th) with all current additions and amendments.

        - IEC 391	 Marking of Insulated Conductors

        - IEC 445 Equipment Terminals (Identification of Equipment Terminals and Terminations of Certain Designated Conductors).

        - IEC 446 Identification of Bare Conductors by Colors or Numerals.

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years’ period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

        - Provide samples of all proposed devices, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Method Statement and Manufacturer’s Instructions: Indicate application conditions and limitations of use stipulated by product Testing Agency and include instructions for storage, handling, protection, examination, preparation and installation of the product.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations of tagged devices; include tag numbers.

      - QUALIFICATIONS

        - Manufacturers: Firms regularly engaged in manufacture of items the types, sizes and ratings required, whose products have been in satisfactory use in similar service for not less than 5 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - QUALITY ASSURANCE

        - All items of Electrical Identification shall comply with the requirements of BS and Local Standards.

      - DELIVERY, STORAGE, AND HANDLING

        - Requirements of Division 01.

        - Accept identification products on site in original containers. Inspect for damage.

        - Accept materials on site in original factory packaging, labeled with manufacturer's identification, including product density and thickness.

        - Protect insulation from weather and construction traffic, dirt, water, chemical, and mechanical damage, by storing in original wrapping.

      - ENVIRONMENTAL REQUIREMENTS

        - Install labels, nameplates only when ambient temperature and humidity conditions for adhesive are within range recommended by manufacturer.

      - SPARE PARTS

        - Supply as maintenance stock, additional labels and name plates of all types and sizes, amounting to one unit for every 10 installed units, but not less than two units of each type and size.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

- PRODUCTS

      - NAMEPLATES AND LABELS

        - Nameplates and labels shall be engraved on a three-layer 2 traffolyte plate having minimum thickness of 2 mm, securely screwed to the housing and have black letters on white background in Arabic and English.

        - The name plates and labels shall be required for each electrical distribution board, control panels, equipment enclosures, substation equipment, disconnect switches and equipment cabinets.

        - Lettering shall be block capitals standing:

          - 6 mm high for identifying individual equipment and loads.

          - 10 mm high for identifying grouped equipment and loads.

        - Labels using embossed adhesive tape with 6mm white letters on black background or transparent adhesive tape with 6 mm black letters, as selected by the Engineer, shall be used for identification of individual wall switches, receptacles, low current outlets, speakers, control device stations, junction/pull boxes, electrical boxes and fittings, etc.

      - WIRE MARKERS

        - Wire markers shall be split sleeve or tubing type.

        - The wire markers shall be required for each conductor at panel board gutters, pull boxes, outlets, junction boxes and each load connection.

        - All power and lighting circuits, branch or feeder circuits and control circuits shall require wire markers.

      - COLOUR CODING OF RACEWAYS

        - Provide color bands with printed description of each system, minimum 75 mm wide for all cable trays/ladders and trunking runs. These color bands shall be applied at each electrical distribution/panel board, low current system control panels and junction box locations and at 15 m centers within an area.

        - Provide color bands with printed description of each system, minimum 25 mm wide for conduits up to 25 mm in diameter and one-half the conduit diameter for larger conduits, applied at panel and pull box locations, within each room, and at 6 m centers within an area.

        - Following color banding shall be used for the raceways of various electrical systems, however subject to final decision of the Engineer. Color bands for the electrical systems not described here shall be as agreed on site:

          - Lighting: gray.

          - Normal Power: brown.

          - Essential Power: black

          - Earthing: green.

          - Fire alarm: red.

          - Telephone: blue.

          - Sound: yellow.

          - Data: purple.

          - Television: rust.

      - CIRCUIT IDENTIFICATION CHARTS

        - Individual circuit identification charts shall be provided for all panel boards, distribution boards, control panels, etc. giving following information as a minimum.

          - Circuit numbers

          - Phase

          - Load names with location.

          - Connected load.

          - Outgoing terminal numbers.

          - Sizes and types of protective devices.

          - Sizes and types of incoming and outgoing cables.

          - Contacts location references of relays and other control devices (if any).

        - Charts shall be typed on A4 size sheets. They shall be enclosed in a clear plastic envelope and shall be securely fixed to the inside cover of the unit. Additional copies of the charts shall be included in the Operation and Maintenance Manuals.

      - CABLE IDENTIFICATION TAGS

        - All cables which exit from manholes, vaults, handholes, and transformer or switch enclosures shall be properly tagged or labeled. Tags shall be permanent, non-corrodible and clearly readable. Tags should include the information listed below for the various circuit categories:

          - Primary Cables – MV.

          - Feeder Name

          - Voltage

          - Phase (for single conductor cables)

        - Cable identification tags for wire and cable circuits shall be of an opaque nylon material arranged to include a marker plate, non-releasing nylon ties, and cable fastening tail. One side shall be roughened to hold black nylon permanent ink. Identification shall be permanent and waterproof. The holding device shall be designed to allow the fastening tail to pass around the cable through the holding device, and prevent removal of the tail without cutting it loose from the marker. Cable identification shall be inscribed in Arabic and English.

      - CABLE WARNING TAPES

        - For buried LV and MV cables use warning tapes according to the standard practice of Electricity Supply Authority and applicable international standards.

        - Cable warning tapes shall be of polythene, not less than 150 mm wide and at least 0.25 mm thick. They shall be yellow in color for LV and MV cables and bear the continuously repeated legend – “CAUTION ELECTRIC CABLE BELOW” or similar in English and Arabic, in black letters not less than 30 mm high.

        - For buried low current/communication cables or duct banks, use warning tapes as per the standard practice of Local Telecom Supplier and applicable international standards.

      - CABLE MARKERS

        - Buried cables shall be permanently identified by concrete markers. The markers shall be 600 mm square x 100 mm thick with impressed character; they shall be made of grade 20 concrete, with 10 mm aggregate. The impressed characters shall be in English and Arabic and worded "HV CABLE" or "LV CABLE" as appropriate together with circuit details as required for proper identification. In addition, the word “JOINT” shall be added to above words, where applicable.

        - Except where cables are buried, located in switchrooms, in ducts and spaces designated solely for electrical services, or have orange oversheaths; they shall be identified by adhesive bands colored orange, complying with standards and codes of practice mentioned elsewhere in the Specifications. The bands shall be not less than 100 mm long, located at least once within each separate compartment through which cables pass and at intervals not exceeding 12 m.

        - Except where cables are buried or enclosed in conduit, trunking or ducting; they shall be permanently identified by discs. The discs shall be of laminated plastic materials with black character on white; character shall be not less than 3 mm high. The inscription shall indicate the nominal voltage, the designation of the load, the number and cross sectional area of cores and the rated voltage of the cable.

        - Cables identification discs shall be attached to the cables with ties. Disc shall be located within 500 mm of terminations and joints, at least once within each separate compartment through which the cable passes, and at intervals not exceeding 24 m, they shall coincide with the colour bands.

      - EQUIPMENT WARNING/DANGER SIGNS

        - For external use, pressure sensitive danger signs shall be used. Dimensions shall be as approved by the Engineer. The signs shall be heavy duty vinyl with a self-adhesive backing which can be applied to curved or irregular surfaces. Danger signs shall be weather-resistant and shall not discolor or deteriorate with age.

        - Danger signs shall be inscribed with the equipment voltage level along with an internationally recognized danger sign.

        - Warning/Danger signs made of red plastic (vinyl) with white letters at least 25 mm high reading "DANGER High Voltage" shall be fixed to the entrance doors of all MV switchgear and transformer rooms.

        - Warning/Danger signs made of red plastic (vinyl) with white letters at least 15 mm high reading "DANGER 400V"or “DANGER 230V” as appropriate, shall be fixed to the lids, covers or doors of any equipment which contains terminals or conductors connected to more than one phase of a low voltage supply.

        - All signs shall be in English and Arabic.

      - LANGUAGE

        - The Arabic and English languages shall be used for all labeling and charts.

- EXECUTION

      - PREPARATION

        - De-grease and clean surfaces to receive nameplates and labels.

      - INSTALLATION

        - Install warning and descriptive labels as follows:

          - Metallic surfaces using stainless steel or chromium plated bolts and/or self-tapping screws.

          - Concrete surfaces or masonry walls using and brass wood screws.

          - Timber surfaces using minimum 6 mm countersunk brass screws.

          - All insulated enclosures using an approved plastic welding adhesive.

        - The danger sign and identification number shall be affixed to the front or access doors of all transformers and switches. For equipment with two doors the danger sign shall be mounted on the left door with the identification number mounted on the right door. Both the danger sign and the identification number shall be centered 300 mm below the top edge of the doors and on the vertical centerline of each door.

        - On equipment with only one access door, the danger sign and the identification number shall be centered on the vertical centerline of the door, with the horizontal center line of the danger sign 300 mm below the top edge of the door and the horizontal center line of the identification number 250 mm below the danger sign centerline.

        - Locate cable markers at every point where cable(s) enter a building, sub-station, distribution/feeder pillar; at each joint, change of direction, road/pathway crossing, etc.  Cable markers shall also be provided along the straight runs (route) of the cable(s) at the interval not exceeding 30 m.

- END OF SECTION