- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Operation, maintenance and testing/commissioning of electrical systems.

          - Operation and Maintenance Manuals.

      - REFERENCES

        - All inspections and tests shall be in accordance with the following applicable codes and standards except as provided otherwise herein:

          - International Electro-Technical Commission – IEC

          - British Standards – BS

          - European Standards - EN

          - Institute of Electrical and Electronic Engineers – IEEE

          - National Fire Protection Association – NFPA

          - Local codes and ordinances

          - Applicable Independent Testing Associations Specifications

          - Operator requirements.

        - All inspections and tests shall utilize the following references:

          - Project design specifications

          - Project design drawings

          - Manufacturer’s instruction manuals applicable to each particular apparatus.

      - GENERAL

        - Access shall be afforded at all times to the Engineer to enable him to inspect the Electrical Equipment.

          - Upon completion of the Electrical Equipment installation or part of the installation, the carry out and be responsible for testing and commissioning, in stages if required, to ensure that it is in proper working order and capable of performing all of its functions in accordance with the Specification and to the satisfaction of the Engineer. Any Electrical Equipment damaged in commissioning shall be replaced and retested by the Contractor at his own expense to the satisfaction of the Engineer.

          - All testing shall be carried out according to the requirements of the relevant standards and regulations as may be stated or implied in the Specification or otherwise agreed by the Engineer in writing.

          - Submit for Engineer's approval, no later than 6 weeks prior to the commencement of testing and commissioning, a schedule of all Electrical Equipment tests and commissioning procedures to be carried out to prove that the Electrical Equipment complies with the requirements of the Specification together with proposed programmer for such testing and commissioning.

          - Tests shall not commence before the schedule of tests has been approved and such other tests as may be required by the Engineer shall be included within the schedule of tests.

          - Give to the Engineer in writing at least ten days' notice of the date by which he will be ready to make the specified tests on completion of installation. Unless otherwise agreed the tests shall take place within seven days after the said date on such day or days as the Engineer shall in writing notify the Contractor.

          - The tests shall as far as possible be carried out under normal working conditions to the satisfaction of the Engineer and shall extend over such periods as he may direct.

          - Provide all skilled labor, supervision, consumables, apparatus and instruments required for commissioning and testing and within a reasonable time thereafter furnish to the Engineer a total of six certificates of all tests performed and accepted, signed by the Contractor, or an authorized person acting on his behalf, as prescribed in the appropriate regulations and specifications.

          - When any part of the Electrical Equipment fails to pass the specified tests, further tests shall be repeated, if required by the Engineer. The Contractor shall, without delay, put in hand such modifications as are necessary to meet the requirements as described in the Contract and any expense which the Owner may have incurred by reason of such further tests may be deducted from the Contract price.

          - Acceptance shall not in any way absolve the Contractor of his responsibility for the performance of the Electrical Equipment after erection as a complete working system in all respects.

          - Each completed system within the installation shall be tested as a whole under normal site operating conditions to ensure that each component functions correctly in conjunction with the rest of the system.

        - Program, oversee, co-ordinate and record all the testing and commissioning of the electrical systems in co-ordination with those elements undertaken by the mechanical services Contractor. The electrical Contactor shall allow for liaising and attendance and providing all necessary test and general data information at the correct times.

        - For remote monitoring/controls, comply with the requirements as given in Section 25 50 00.

        - The systems shall undergo phases of testing and commissioning, in accordance with the following: -

          - Phase 1.	Works testing and quality assurance of elements;

          - Phase 2.	Site installation, wiring, checks, performance and operational tests for all elements;

          - Phase 3.	Sub system group operational tests/performance tests;

          - Phase 4.	Complete system operational and performance tests on dummy loads;

          - Phase 5.	Complete system operational and performance tests on actual loads.

        - All the electrical systems, whether mentioned in this section or not, shall be subject to testing and commissioning.

        - All tests listed under the heading of “Field Quality Control” in various sections of Division-26 of these Specifications shall be conducted in the presence of and performed up to the full satisfaction of the Engineer. All the results/test reports shall be submitted in bound form for Engineer’s approval.

        - All Electrical Equipment and integral systems shall be commissioned in accordance with the relevant standards and regulations given in the Specification and to the recommendations of specialist suppliers (e.g. Grounding Switchboards, Standby Generators, Fire Detection and Alarm System, Cables, etc.), as well as to the Local Authorities/ Utilities acceptance; the Contractor is responsible for getting A Report of The State Acceptance Commission which shall be part of the  close out submittals the Contractor shall provide for all electrical systems.

        - Full operational tests shall be carried out on all systems to demonstrate that they operate in accordance with the requirements of the Specification.

        - Perform cause and effect tests, final tests and submit to the Engineer for Approval.

        - Tests mentioned in these specifications are the minimum required tests, all other tests mentioned in related international standards are required.

      - ELECTRICAL TESTING

        - Tests of the installation shall be carried out in the following sequence:

          - Protective conductor continuity, including main and supplementary equipotential bonding.

          - Earth electrode resistance.

          - Measurement of insulation resistance including site-built assemblies and distribution cables.

          - Check of protection by electrical separation, barriers and enclosures.

          - Measurement of the insulation on non-conducting floors and walls.

          - Check of phase rotation.

          - Verification of polarity.

          - Measurement of earth fault loop impedance.

          - Test of operation of residual current devices.

          - All external distribution cables, low voltage in accordance with the relevant standard(s).

          - Fault simulation on protective devices or control system of stand-by generator, transformers, power distribution boards, etc.

          - Load test on standby generator, sub-station, power distribution boards, panel boards, ATS, synchronizing panels, etc.

      - LOW CURRENT SYSTEMS TESTING

        - All low current systems such as Data networks, telephone, public address, fire detection and alarm, A/V systems, Security Systems, etc. shall be tested as specified herein or recommended by the manufacturers.

        - Submit to the Engineer in writing the procedure to test these systems as a whole for the site.

        - At the completion of these special systems installation for each facility, these shall be tested individually for each facility then it should be tested with their main control panel, such as fire detection and alarm, telephone etc. so that to see the good performance of these systems as a whole.

      - LV POWER DISTRIBUTION BOARD / PANELBOARDS

        - Design tests of;

          - Degree of Protection.

          - Rated continuous current.

          - Short circuit current.

          - Enclosure dielectric.

          - Test of apparatus i.e. circuit breaker and earthing switch

        - Production Functional tests of:

          - Dielectric.

          - Mechanical operation.

          - Grounding.

          - Control wiring.

          - Electrical operation.

          - Energy Meter Testing and Calibration.

          - C.T. and P.T. Insulation Testing and Ratio Verification.

          - Cable’s Insulation

          - Cable’s Termination Kit’s Installation & Jointing etc.

          - Earth Testing.

      - EMERGENCY POWER GENERATION SYSTEM

        - Field erected fuel piping shall be tested with air pressure and proven right at 150 % of the working pressure for a period of two hours.

        - Factory tests shall be performed in accordance with the following requirements:

          - Unless otherwise directed, all tests shall be performed in the presence of the Engineer.

          - Each assembled engine and generator shall be tested in accordance with the manufacturer's customary practice.

          - All components shall be checked, lube-oil leaks shall be remedied.

        - Following the complete installation of the generating unit and its associated equipment, field tests shall be conducted. Provide all instruments and supplies required for the tests.  Fuel instruments and instrumentation procedures to be followed shall be appropriate for the tests to be performed.  Prior to the startup of any generating units, the Contractor shall demonstrate to the satisfaction of the Engineer that all piping systems have been cleaned.

        - Sequence of Field Tests:

          - The Gen set shall be tested at rated ambient temp and altitude

          - Check all engine and driven unit mounting bolts.

          - Check alignment of engine and generator by dial indication.

          - Check generator motor air gap.

          - Check generator and exciter insulation resistance with an insulation resistance tester.

          - Perform engine manufacturer's recommended pre-starting checks.  This shall include a test of the prestart lube-oil pump to determine if adequate oil pressure is provided.

          - Start engine and make engine manufacturer's after starting checks during a reasonable run-in or warm-up period.

          - Operate generator with step loads of 25%, 50%, 75% and 100% for 8 hours/day.  Record data hourly, including current, voltage, frequency kW and temperature information.  A load bank has to be provided by the Contractor.

          - Increase engine speed by means of the governor.  Check speed at which over-speed device trips.

          - Check functioning of high coolant temperature trip by restricting air into the radiator.

          - Shutdown engine and record pressure at which low oil pressure device trips.

        - Checks to be made during field testing:

          - During the tests, all operations of which the controls on the panel and at the switchboard are capable shall be performed to assure that all controls are functioning in a satisfactory manner.

          - At several points during the tests, each instrument on the switchboard and engine panel shall be observed to assure that all instruments and gauges are functioning properly.

          - During the tests, all Auxiliary and accessory equipment, all valves including pilot valves, and the injection pumps shall be checked to assure proper operation.

          - During the 100 % load test, pyrometer reading of each cylinder of each engine shall be taken and recorded at 1/2-hour intervals.

        - After completion of the tests, a general inspection shall be made for:

          - Leaks in the engine, piping systems, tanks, etc.

          - Blow-by.

          - Crankcase contamination.

          - Crankshaft misalignment.

          - Generator misalignment and damage to generator bearings.

      - UPS SYSTEM

        - All routine tests specified in IEC 146-4 shall be carried out, together with tests listed below, both at the factory testing and on site.  The UPS Supplier shall allow for providing a 110% load bank to fully commission the system following completion.  Full load and battery discharge tests are required on site.  The load bank shall be capable of 110% kW loading at 0.7 power factor.

          - Synchronization (dual variable voltage and variable frequency supplies will be required for this purpose at the factory and on site).

          - Rated stored energy time.

          - Rated restored energy time.

          - Battery ripple current.

          - Overload capacity.

          - Restart.

          - Audible noise.

          - Earth fault test.

          - Full load test.

          - Tests to prove alarm and control indication and auxiliary devices.

        - Factory tests and on-site tests shall include but not be limited to: -

          - Checking and verifying output voltage, output frequency, and input power factor with 100% step load against 0.7 load power factor and against a high harmonic load.  (Note: A rectifier input of another UPS may be used to simulate this at works).

          - Checking and verifying output current.

          - Checking and verifying synchronization range.

          - Checking and verifying output, harmonic content both total and each harmonic up to 19th, both in balanced and imbalanced load conditions with 12% improved harmonic support at 0.7 pf.

          - Checking and verifying overload limits of 10%, 25% and 50% of full load.

          - Checking and verifying short circuit and fuse clearing capability.

          - Checking and verifying efficiency on loads of 50%, 75% and 100% of full load.

          - Checking and verifying heat losses at loads of 50%, 75% and 100% of full load.

          - Checking and verifying noise levels at loads of 25%, 50%, 75% and 100% of full load.

          - Checking and verifying remote alarms, contacts and inputs.

          - Battery Chargers and DC Isolation Switchgear.

          - Check and verify output float voltage.

          - Check and verify output boost voltage.

          - Check and verify output current.

          - Check and verify ripple factor.

          - Check and verify operation of controls, alarms.

        - The paralleling switchboard shall be tested to the requirements of BS 5486, and if not tested at factory with the UPS modules, to be fully functional tested with full simulation of all digital and analogue inputs. This is to include all auto bypass and synchronizing control simulation.

        - The supplier shall allow for up to 2 persons to witness the testing at the manufacturer’s works including travel, accommodation and subsidence during a minimum 2-day period.  The supplier shall also allow for his commissioning engineer, who is to carry out the on-site testing to observe and witness the full factory testing of the units.

      - FIRE DETECTION AND ALARM SYSTEM

        - Wiring runs shall be tested for continuity, short circuits and grounds before system is energized.  Resistance, current and voltage readings shall be made as Work progresses.

        - A systematic record shall be maintained of all readings using schedules or charts of tests and measurements.  Areas shall be provided on the logging form for readings, dates and witnesses. The Engineer shall be notified before the start of the required tests. All items found at variance with the drawings or this specification during testing or inspection by the Engineer, shall be corrected.

        - Test reports shall be delivered to the Engineer as completed.

        - All test equipment, instruments, tools and labor required to conduct the system tests shall be made available by the installing Contractor.  The following equipment shall be a minimum for conducting the tests:

          - Ladders and scaffolds as required to access all installed equipment.

          - Multimeter for reading voltage, current and resistance.

          - Intelligent device programmer/tester.

          - Two-way radios, flashlights, smoke generation devices and supplies.

          - Laptop computer with programming software for any required programmed revision.

          - A manufacturer recommended device for measuring air flow through air duct smoke detector sampling assemblies.

          - Decibel meter.

        - In addition to the testing specified to be performed by the installing Contractor, the installation shall be subject to test by the Engineer.

        - A written acceptance test procedure (ATP) for testing the fire alarm system components and installation will be prepared by the Contractor and submitted for review and approval to the Engineer in accordance with NFPA 72, and this specification. The Contractor shall be responsible for the performance of the ATP, demonstrating the function of the system and verifying the correct operation of all system components, circuits, and programming.

        - A programmer matrix shall be prepared by the installing Contractor referencing each alarm input to every output function affected as a result of an alarm condition on that input. In the case of outputs programmed using more complex logic functions involving "any", "or", "not", "count", "time", and "timer" statements; the complete output equation shall be referenced in the matrix.

        - A complete listing of all device labels for alphanumeric annunciator displays and logging printers shall be prepared by the installing Contractor prior to the ATP.

        - In conducting the ATP, the Engineer shall request demonstration of any or all input and output functions. The items tested shall include, but not be limited to, the following:

          - System wiring shall be tested to demonstrate correct system response and correct subsequent system operation in the event of:

            - Open, shorted and grounded intelligent analog or network signaling circuits.

            - Open, shorted and grounded conventional zone circuits.

            - Open, shorted and grounded speaker telephone circuits.

            - Primary power or battery disconnected.

            - Intelligent device removal.

            - Incorrect device at address.

            - Printer trouble, off line or out of paper.

          - System evacuation alarm indicating appliances shall be demonstrated as follows:

            - All alarm notification appliances actuate as programmed.

            - Audibility and visibility at required levels.

          - System indications shall be demonstrated as follows:

            - Correct message display for each alarm input at the control panel, each remote alpha-numeric display and each CRT terminal.

            - Correct annunciator light for each alarm input at each annunciator and colour graphic terminal as shown on the Drawings.

            - Correct printer logging for all system activity.

          - System off-site reporting functions shall be demonstrated as follows:

            - Correct zone transmitted for each alarm input.

            - Trouble signals received for disconnect.

          - Secondary power capabilities shall be demonstrated as follows:

            - System primary power shall be disconnected for a period of time as specified herein.  At the end of that period, an alarm condition shall be created and the system shall perform as specified for a period as specified.

            - System primary power shall be restored for forty eight hours and system charging current shall be normal trickle charge for a fully charged battery bank.

            - System battery voltages and charging currents shall be checked at the fire alarm control panel using the test codes and displayed on the LCD display.

          - Fireman's HVAC override system functions shall be demonstrated as follows:

            - Operation of key lockout switch preventing unauthorized operation of controls.

            - On/Off controls of each controlled element and test of interaction of other automatic and manual control functions while in the over-ride mode.

            - Correct status display of monitored elements.

            - Correct logging of activity to printer and historical memory as programmed.

        - In the event of system failure to perform as specified and programmed during the ATP procedure, at the discretion of the Engineer, the test shall be terminated. The installing Contractor shall retest the system, correcting all deficiencies and providing test documentation to the Engineer. The Engineer may elect to require the complete ATP to be performed again if, in his opinion, modifications to the system warrant complete retesting.

        - Changes made to a systems configuration program required by the acceptance inspector or to comply with the systems operating parameters shall be validated to insure that in making the software programming change no other part of the systems operation was effected.  The validation shall utilize systems software which meets the requirements of NFPA 72 section 7-1.6 "System Reacceptance Testing" as specified in the NFPA 72 National Fire Alarm Code 1993 edition.  Change validation methods other than that described will not be considered acceptable and shall allow the acceptance inspector to require the complete ATP to be performed again.

      - GROUNDING AND EARTHING SYSTEM

        - Prior to any installation, perform soli resistivity measurements, submit to the Engineer for his approval with full calculations and drawings for proposed earthing and bonding system.

        - Perform grounding resistance tests after installation of the individual Grounding systems in accordance with the Specifications. The Grounding resistance tests shall be carried out in accordance with Section 713-11 of the IEE Wiring Regulations 17th edition and readings obtained officially recorded by all witnessing parties.

        - Prior to connection of Grounding rods to the Grounding system, the Grounding resistance of individual Grounding rod shall be measured by using an approved type of Grounding resistance tester, resistance shall not exceed the 10 Ohm per each rod.

        - After completion of all the connections of Grounding system, the Grounding resistance shall be measured from the Grounding test point in presence of the Engineer.

        - All the Grounding resistance test reports shall be submitted for Engineer’s approval.

        - System’s overall resistant shall not exceed 1 Ohms

      - SAFETY TAGGING PROCEDURES

        - Develop and submit for Engineer’s approval prior to implementation, a safety tagging procedure for use when working on energized systems or to identify systems that have been turned over to operations.

        - Provide plastic tags of minimum dimensions 300 x 200 x 3 mm with appropriate internationally recognized pictorial symbols and statements in Arabic and English languages for use as safety tag. The tags shall be coloured red with white letters or coloured yellow with black letters as approved by the Engineer. The letters shall be at least 20 mm high or more as required. The safety tag shall be provided with fire resistant rope for suspension at suitable locations.

        - Type of safety tags shall include, but not limited to, the following:

          - Refer to the equipment instructions/manual for important information before proceeding.

          - This unit must be accessed only by qualified personnel.

          - Do not switch ON. Work is in progress on other end.

          - Danger – Hazardous AC (or DC) voltage.

          - Danger – AC mains voltage.

          - Danger – Hot surface. Do not touch without taking care.

          - Risk of injury due to high current.

          - Avoid contacting conductors with un-insulated metal objects. Follow safety precautions. Make sure the power is disconnected.

          - Danger – Arcing/Sparking may happen. Risk of eye injury. Always wear safey glasses.

          - Make sure the equipment is grounded before switching ON power.

        - The installation and removal of safety tagging shall be carried out with the permission of an authorized Client’s or Engineer’s representative.

        - Approved type of pad locks shall be provided to lock out any circuit breaker, isolator, switch fuse or a piece of equipment to prevent accidental turn ON or turn OFF. The keys shall be in the custody of an authorized Owner’s representative.

      - INSULATION

        - Check the insulation resistance to ground and phase to phase of all parts of the electrical installation with a Megger Test with all panels, switches, socket outlets and branch circuit wiring installed and connected, but without fluorescent fixtures connected. Complete insulation tests to the Engineer's approval before power is applied to any circuit.

      - LIGHTING

        - Verify the correct lamps, position, electronic ballast/driver   and operation of all fixtures.

        - With all lighting in operation, measure the average illuminance on the floor or tread (by establishing the maximum and minimum levels) in the following locations:

          - Exits, public corridors, corridors leading to exits, electrical equipment rooms, and elevator hoist ways.

          - Offices, storage, service rooms, parking, laundries, kitchens, stairways, W.C., …etc.

          - Every place of assembly.

          - Rooms and areas as directed by the Engineer.

        - With only the emergency lighting in operation, measure the average illumination at exits, public corridors, floor areas where the public may congregate and other rooms and areas as directed by the Engineer.

        - Take readings at night, with no outside light contribution.

        - Take readings with a cosine corrected portable digital illuminance meter, or with a video camcorder with suitable software for illuminance measurements. Measuring instruments shall be tested, calibrated and certified accurate to within 2%.

        - Submit technical, testing and calibration data as well as certification on the photometer.

        - Plot lighting results on a set of reproducible plans for review by the
Engineer and submission to the authorities.

- OPERATIONS AND MAINTENANCE (O&M) MANUALS

      - GENERAL

        - The Contractor is to provide completed Operation and Maintenance Manuals to the Principals Authorized Person prior to Completion or the date nominated in the approved Commissioning and Handover Plan. This is a condition precedent to payment for any Completion Amounts due under the Contract.

      - OBJECTIVES

        - The objectives of the Operations and Maintenance Manuals are:

          - To be of sufficient detail to enable the Principal to take over any maintenance, operation or use of the works and to do so in a safe, effective and efficient manner.

          - To enable progressive and timely development and checking of the Manuals in advance of any completion milestones.

          - To be fully completed and finalized prior to the Principals occupation, use or acceptance of the works.

          - To be developed in standardized and fully electronic data format suitable for upload to the Principals Asset and Data Management Systems.

          - To enable complete financial reconciliation of the assets and works showing element and asset costs, life expectancy costs and the like.

      - CAPTURE OF ASSET, MAINTENANCE AND OPERATIONS DATA

        - Contractors must progressively capture and input all relevant data into the O&M system in a timely manner during the contract term and prior to any handover of the works.

        - Contractors are required to check and correct the data progressively.  Where the works are to be completed and handed over to the Principal in stages or separable portions the O&M Manuals are to be completed to sufficient detail and content to enable the Principal to assume its responsibilities for the ongoing operation and maintenance of the completed works.

      - QUALITY ASSURANCE PROCESS STANDARD O&M HEADINGS

        - O&M Manuals are to follow the standard headings shown below to ensure consistency for all elements of the works:

          - Introduction & Scope: Overview and description of the systems, the approach taken and other relevant information to ensure the client has an understanding of the equipment and its intended purpose.

          - Assets: Detailed schedule of all financial assets data, maintainable assets data, items and locations all reconciled to the total projects value.

          - Maintenance: Detailed instructions and frequency to ensure proper function of the assets.

          - Operations Data:  Detailed instructions for safe and efficient operation of the assets, including general cleaning, proper use and function of the assets/systems and relevant suppliers documentation.

          - Spare Parts: Listed items or components required to complete maintenance or operation tasks or for replacements.

          - Warranty and Certificates: Descriptions of all warranties and (both contracted and procured through suppliers) for the assets and descriptions of any certificates issued as part of the works including uploaded copies of all relevant documents.

          - Help and Contact: Details of any relevant contractors, suppliers and the like who may be used by the owner to support the operation and maintenance of the assets.

          - Drawings and Reference: Lists of all final as built drawings, specifications and other relevant documents forming the final contract scope and other relevant attachments - like product manuals, specifications and the like relevant to the proper operation and maintenance of the works.

      - HANDOVER OF ASSET, MAINTENANCE AND OPERATIONS DATA

        - The Contractor is to advise the Principal and or the Authorized Person when the Operations and Maintenance data is complete and accurately reflects the works.

        - The Contractor is to complete the draft O&M Manuals 28 days in advance of Handover of the Works or parts thereof or in accord with the approved Commissioning and Handover Plan whichever is the earlier date.

        - Should the Principal and or the Authorized Person identify any errors or omissions in the submitted data then within the time period stated in the approved Commissioning and Handover Plan or the issued Defect Notice the Contractor is required to rectify any items and to pay all such costs that may be incurred to update the final data.

      - DOCUMENT COMPLETION

        - The Contractor must integrate the collection of asset data documents, and their subsequent production and submission in accord with the timing set out in the approved Commissioning and Handover Plan (including Inspection and Test Plans and Staged works handover), with progressive development of documents in electronic form.

        - The number of electronic copies of O&M Manuals shall be as stated in the approved Commissioning and Handover Plan or in the absence of a stated number 1 copy for each defined recipient in the Contractors are to advise the Principal or where responsibility for verification of O&M Manuals is vested with the Contractor or another Party when Manuals are at draft stage and ready for review.Nominated personnel from the Principal, and or Responsible Party in accord with the approved Commissioning and Handover Plan shall access the on-line O&M Manuals and provide comments or directions for any corrections as needed.

        - The Contractor will update the O&M Manual data in accord with the directions issued and the stated timetable and notify the Principal or Responsible Party of satisfactory completion.

        - When notified by the Principal or Responsible Party of completion of all O&M Manuals the Contractor is to direct to close on-line access (to prevent further alteration to the approved data) and transfer all O&M Data to CD versions for Handover.

      - COMPLIANCE WITH LAWS, STANDARDS AND SPECIFICATIONS

        - The Contractor shall check and verify that all data and attached files and documents that form the completed O&M Manuals comply with the relevant Laws, Standards, Codes and Specifications applicable to the works to enable the proper operation and maintenance by the Principal and or its appointed agents of the completed works.

      - WORK-AS-EXECUTED DRAWINGS

        - The Contractor is to provide to the Principal work-as-executed drawings in electronic formats for Subcontract and Supplier packages showing the completed works as constructed for that stage or portion of the works. Formats are to be PDF and CAD or other format as approved by the Principal.

        - Ensure the content, accuracy and level of detail of work-as-executed drawings are equivalent to those in the detail design drawings used for construction and are sufficient to describe and to ensure the efficient operation of the assets created under the Contract. Where required to describe the Works, include digital photographs of specific aspects of the Works in work-as-executed drawings or operations and maintenance manuals.

        - Include in work-as-executed drawings a survey drawing indicating the position of the Works relative to a primary survey grid. Certify survey drawings using a Registered Surveyor where required by the Principal.

        - All work as executed and as-built documentation must be in accord with the Specification. Verify each drawing certifying accuracy, completeness, correctness and compliance with CAD conventions.

        - All work as executed and as-built documentation must be uploaded into the system.  All Attached files to be adequately described in  Heading and Description boxes per Contract Specification including Drawing title, number, short description of the works, location ie Building No etc (similar to drawing register).  Where a Zip file is used all contained files and their titles are to be shown in the Description box with sufficient detail to allow easy assessment of each files contents.

      - HARD COPY FORMAT

        - Where any conflict occurs with any other part of the contract and or specifications in reference to provision of Hard Copy O&M Manuals the Principal in the interests of compliance with Green Building Policy will accept the same number of electronic copies of O&M Manuals in lieu of the number of Hard Copy Manuals nominated.

        - Manuals shall be bound in a three ring hard-backed binder. Front cover and spine of each binder shall have the following lettering done:

OPERATION AND MAINTENANCE MANUAL FOR ELECTRICAL SYSTEMS (PROJECT NAME) (LOCATION) (DATE) SUBMITTED BY (NAME AND ADDRESS OF CONTRACTOR)

        - Provide a master index at the beginning of manual showing items included. Use plastic tab indexes for sections of manual. Each section shall contain the following information for equipment furnished under this contract:

          - Equipment and system warranties and guarantees.

          - Method Statement.

          - Installation instructions.

          - Operating instructions.

          - Maintenance instructions.

          - Spare parts identification and ordering list.

          - Local service organization, address, contact and phone number.

      - ELECTRONIC COPY FORMAT

        - The Contractor is to provide to the Principal the specified number of copies of the WebFM electronic O&M Manuals in CD or DVD disks containing all O&M Manual data, attached files and documents transferred from the on-line web site.  Disk Media are to be packaged in a suitably bound Disk Case.  Disks and Case are to be fully labeled with the following:

          - Project Name (Front Case cover and Spine, All Disk Media)

          - Contractor Name and contact details (logo may be inserted)

          - Compiled date (date when O&M Manuals data transferred to Disk Media)

          - Contents List (include list of all trade manuals in order)

          - Installation instructions (inside front Case Cover)

        - All O&M Manuals are to be supplied in standalone MS Access database and PDF formats as single electronic systems with suitable hyperlinks to all associated files and documents for easy retrieval and use by the Principal.

        - The number of electronic copies of O&M Manuals shall be as stated in the approved Commissioning and Handover Plan or in the absence of a stated number 1 copy for each defined recipient in the approved Commissioning and Handover Plan.  A minimum of 2 CD Copies are to be supplied.

- END OF SECTION