SECTION 23 3100
HVAC DUCTS AND CASINGS

PART 1 GENERAL

- SECTION INCLUDES

- Metal ductwork.

- Nonmetal ductwork.

- Casing and plenums.

- Duct cleaning.

- RELATED REQUIREMENTS

- Section 03 3000 - Cast-in-Place Concrete.

- Section 07 8400 - Firestopping.

- Section 09 9113 - Exterior Painting: Weld priming, weather resistant, paint or coating.

- Section 09 9123 - Interior Painting: Weld priming, paint or coating.

- Section 23 0593 - Testing, Adjusting, and Balancing for Mechanical Works.

- Section 23 0713 - Duct Insulation: External insulation and duct liner.

- Section 23 3300 - Air Duct Accessories.

- Section 23 3600 - Air Terminal Units.

- Section 23 3700 - Air Outlets and Inlets.

- REFERENCE STANDARDS

- ASHRAE (FUND) - ASHRAE Handbook - Fundamentals; 2013.

- ASTM A36/A36M - Standard Specification for Carbon Structural Steel; 2014.

- ASTM A653/A653M - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process; 2015.

- ASTM A666 - Standard Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar; 2015.

- ASTM A1008/A1008M - Standard Specification for Steel, Sheet, Cold-Rolled, Carbon, Structural, High-Strength Low-Alloy, High-Strength Low-Alloy with Improved Formability, Solution Hardened, and Bake Hardenable; 2015.

- ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials; 2015a.

- ICC-ES AC01 - Acceptance Criteria for Expansion Anchors in Masonry Elements; 2012.

- ICC-ES AC106 - Acceptance Criteria for Predrilled Fasteners (Screw Anchors) in Masonry Elements; 2012.

- ICC-ES AC193 - Acceptance Criteria for Mechanical Anchors in Concrete Elements; 2015.

- NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilating Systems; National Fire Protection Association; 2015.

- NFPA 96 - Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations; National Fire Protection Association; 2014.

- SMACNA (DCS) - HVAC Duct Construction Standards Metal and Flexible; Sheet Metal and Air Conditioning Contractors' National Association; 2005.

- SMACNA (FGD) - Fibrous Glass Duct Construction Standards; Sheet Metal and Air Conditioning Contractors' National Association; 2003.

- SMACNA (KVS) - Kitchen Ventilation Systems and Food Service Equipment Fabrication & Installation Guidelines; Sheet Metal and Air Conditioning Contractors' National Association; 2001.

- SMACNA (LEAK) - HVAC Air Duct Leakage Test Manual; 2012, 2nd Edition.

- UL 181 - Standard for Factory-Made Air Ducts and Air Connectors; Underwriters Laboratories Inc.; Current Edition, Including All Revisions.

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements, for submittal procedures.

- Product Data: Provide data for duct materials.

- Calculations showing each system's pressure class.

- Shop Drawings: Indicate duct fittings, particulars such as gages, sizes, welds, and configuration prior to start of work for all duct systems. The drawings must indicate pressure class for each system.

- Samples: Submit two samples of typical shop fabricated duct fittings.

- Manufacturer's Certificate: Certify that installation of glass fiber ductwork meet or exceed specified requirements.

- Test Reports: Indicate pressure tests performed. Include date, section tested, test pressure, and leakage rate, following SMACNA (LEAK).

- Manufacturer's Installation Instructions: Indicate special procedures for glass fiber ducts.

- Project Record Documents: Record actual locations of ducts and duct fittings. Record changes in fitting location and type. Show additional fittings used.

- QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience, and approved by manufacturer.

- Installer Qualifications: Company specializing in performing the type of work specified in this section, with minimum five years of experience.

- FIELD CONDITIONS

- Maintain temperatures within acceptable range during and after installation of duct sealants.

PART 2 PRODUCTS

- DUCT ASSEMBLIES

- Regulatory Requirements: Construct ductwork to NFPA 90A standards.

- Ducts: Rectangular galvanized steel, unless otherwise indicated.

- Fan systems with operating pressure below 500 Pa shall have a pressure class 500 Pa (2 inch w.g) and a leakage class of 24.

- Fan systems with operating pressure below 750 Pa and higher than 499 Pa shall have a pressure class 750 Pa (3 inch w.g) and a leakage class of 12.

- Fan systems with operating pressure below 1000 Pa and higher than 749 Pa shall have a pressure class 1000 Pa (4 inch w.g) and a leakage class of 6.

I. Fume Hood Exhaust: 750 Pa (3 inch w.g.) pressure class, galvanized steel

- MATERIALS

- Galvanized Steel for Ducts: Hot-dipped galvanized steel sheet, ASTM A653/A653M FS Type B, with G90/Z275 coating.

- Joint Sealers and Sealants: Non-hardening, water resistant, mildew and mold resistant.

- Type: Heavy mastic or liquid used alone or with tape, suitable for joint configuration and compatible with substrates, and recommended by manufacturer for pressure class of ducts.

- Surface Burning Characteristics: Flame spread index of zero and smoke developed index of zero, when tested in accordance with ASTM E84.

- Hanger Rod: ASTM A36/A36M; steel, galvanized; threaded both ends, threaded one end, or continuously threaded.

- Hanger Fasteners: Attach hangers to structure using appropriate fasteners, as follows:

- Concrete Wedge Expansion Anchors: Complying with ICC-ES AC193.

- Masonry Wedge Expansion Anchors: Complying with ICC-ES AC01.

- Concrete Screw Type Anchors: Complying with ICC-ES AC193.

- Masonry Screw Type Anchors: Complying with ICC-ES AC106.

- DUCTWORK FABRICATION

- Fabricate and support in accordance with SMACNA (DCS) Duct Construction Standards and as indicated.

- Provide duct material, gages, reinforcing, and sealing for operating pressures indicated.

- Construct T's, bends, and elbows with radius of not less than 1-1/4 times width of duct on centerline. Where not possible and where rectangular elbows must be used, provide air foil turning vanes of perforated metal with glass fiber insulation.

- Provide turning vanes of perforated metal with glass fiber insulation when acoustical lining is indicated.

- Increase duct sizes gradually, not exceeding 15 degrees divergence wherever possible; maximum 30 degrees divergence upstream of equipment and 45 degrees convergence downstream.

- Fabricate continuously welded round and oval duct fittings in accordance with SMACNA (DCS).

- MANUFACTURED DUCTWORK AND FITTINGS

- Flexible Ducts: UL 181, Class 1, aluminum laminate and polyester film with latex adhesive supported by helically wound spring steel wire.

- Insulation: Fiberglass insulation with polyethylene vapor barrier film.

- Pressure Rating: 2.50 kPa (10 inches WG) positive and 250 Pa (1.0 inches WG) negative.

- Maximum Velocity: 20.3 m/sec (4000 fpm).

- Temperature Range: Minus 28 degrees C to 99 degrees C (Minus 20 degrees F to 210 degrees F).

- Transverse Duct Connection System: SMACNA "E" rated rigidly class connection, interlocking angle and duct edge connection system with sealant, gasket, cleats, and corner clips in accordance with SMACNA (DCS).

- CASINGS

- Fabricate casings in accordance with SMACNA (DCS) and construct for operating pressures indicated.

- Mount floor mounted casings on 100 mm (4 inch) high concrete curbs. At floor, rivet panels on 200 mm (8 inch) centers to angles. Where floors are acoustically insulated, provide liner of galvanized 1.21 mm (18 gage, 0.0478 inch) expanded metal mesh supported at 300 mm (12 inch) centers, turned up 300 mm (12 inches) at sides with sheet metal shields.

- Reinforce door frames with steel angles tied to horizontal and vertical plenum supporting angles. Install hinged access doors where indicated or required for access to equipment for cleaning and inspection.

- Fabricate acoustic casings with reinforcing turned inward. Provide 1.52 mm (16 gage, 0.0598 inch) sheet steel back facing and 0.76 mm (22 gage, 0.0299 inch) perforated sheet steel front facing with 2.4 mm (3/32 inch) diameter holes on 4 mm (5/32 inch) centers. Construct panels 75 mm (3 inches) thick packed with 72 kg/cu m (4.5 lb/cu ft) minimum glass fiber insulation media, on inverted channels of 1.52 mm (16 gage, 0.0598 inch) sheet steel.

- FIRE RATED DUCT FOR PRESSURIZATION, SMOKE EXTRACT AND MAKE UP SYSTEMS

- All fire rated duct ratings and specifications must according to UAE Fire and Life Safty Code and should be approved by the Local Civil Defense Authority.

- Duct shall be constructed from galvanized steel sheets in accordance with SMACNA DCS or DW 144(142) and classified to the static pressure class equal to or greater than system pressure.

- Pressurization and make up air duct should be fire outside duct type. Smoke extract duct should be fire inside and outside type duct.

- Duct within a fire compartment should be rated for 1 hour and in accordance with BS 476: Part 24 and BS EN 12101 or ASTM or UL ratings, provided that a motorized fire/smoke damper is installed before connecting to duct that penetrates a fire or smoke compartment.

- Duct that penetrates a fire or smoke compartment must be rated to at least the same duration as the fire barrier it penetrates in accordance with BS 476: Part 24 and BS EN 12101 or ASTM or UL ratings.

- Leakage should not exceed 20% in any case.

- Contractor must submitted drawings defining the different fire ratings of the duct.

- The system must be either UL Listed or tested and certified to BS EN 12101 or to BS476 Part 24 or BS EN 1366-1,8,or 9.

PART 3 EXECUTION

- INSTALLATION

- Install, support, and seal ducts in accordance with SMACNA (DCS).

- Install in accordance with manufacturer's instructions.

- During construction provide temporary closures of metal or taped polyethylene on open ductwork to prevent construction dust from entering ductwork system.

- Fibrous Glass Ducts: Install in accordance with SMACNA (FGD). Obtain manufacturer's inspection and acceptance of fabrication and installation at beginning of installation.

- Flexible Ducts: Connect to metal ducts with adhesive and mechanical fastener.

- Kitchen Hood Exhaust: Provide residue traps at base of vertical risers with provisions for clean out.

- Duct sizes indicated are inside clear dimensions. For lined ducts, maintain sizes inside lining.

- Provide openings in ductwork where required to accommodate thermometers and controllers. Provide pilot tube openings where required for testing of systems, complete with metal can with spring device or screw to ensure against air leakage. Where openings are provided in insulated ductwork, install insulation material inside a metal ring.

- Locate ducts with sufficient space around equipment to allow normal operating and maintenance activities.

- Use double nuts and lock washers on threaded rod supports.

- Connect terminal units to supply ducts directly or with 300 mm (one foot) maximum length of flexible duct. Do not use flexible duct to change direction.

- Connect diffusers or light troffer boots to low pressure ducts with 1.5 m (5 feet) maximum length of flexible duct held in place with strap or clamp.

- Set plenum doors 150 to 300 mm (6 to 12 inches) above floor. Arrange door swings so that fan static pressure holds door in closed position.

- At exterior wall louvers, seal duct to louver frame and install blank-out panels.

- CLEANING

A. Clean duct system and force air at high velocity through duct to remove accumulated dust. To obtain sufficient air, clean half the system at a time. Protect equipment that could be harmed by excessive dirt with temporary filters, or bypass during cleaning.

END OF SECTION