- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Emergency and Exit Lighting self-contained units.

      - REFERENCES

        - CIBSE  The Buildings Lighting Guides issued by the Chartered Institution of Building Services Engineers CIBSE - (UK).

        - BS	         British Standards

        - ICEL 1001      Industry Standard for Emergency Lighting.

        - BS 5266 Pt.1   Code of Practice for Emergency Lighting of Premises

        - IEC               International Electro - technical Commission.

        - NFPA            National Fire Protection Association.

        - Local Codes, Standards and Regulations.

        - Civil Defense Requirements.

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

          - Lighting levels (Lux Levels) calculations for the proposed emergency/ exit light fittings using specialized software.

        - Provide samples of all proposed devices, emergency/ Exit light fittings, lamps, control gears, LED drives,..etc. together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

      - QUALIFICATIONS

        - Manufacturer’s: Firms regularly engaged in the manufacture of lighting fixtures and associated control gear of the types, sizes and ratings required, whose products have been in satisfactory use in similar service for not less than 10 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the Project.

      - QUALITY ASSURANCE

        - All emergency and exit lighting fixtures and associated control gear shall comply with the requirements of listed international and local standards and regulations.

      - DELIVERY, STORAGE AND HANDLING

        - Pack equipment for protection during transportation and storage.

        - Store in dry, clean location.

      - SPARE PARTS

        - Supply as maintenance stock, additional lamps, drivers/ transformers, addressable modules, protective devices of all types and ratings, amounting to one unit for every 10 installed units, but not less than two units of each type and rating.

        - Incase three or less numbers of any above mentioned devices/ consumables of certain rating/ size are installed, a minimum of one for each three numbers additional devices of same rating/ size shall be provided as spare.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 24 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and software and hardware administration of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - All materials specified herein to be of high quality and of proven suitability for the functions they will perform and the conditions they will meet in service.

        - All emergency and exit lights and associated equipment shall be standard products supplied by a single manufacturer.

        - All emergency lighting units and illuminated exit signs that contain a LED lamp, must be provided with the instant-on type or electronic type control gear. These shall be suitable to operate on 240 V or as shown on the Drawings.

      - SELF-CONTAINED EMERGENCY LIGHTING FIXTURES

        - Self-contained emergency lighting fixtures shall provide at least the minimum illumination level required as BS 5266-1/2005 for 3 hours duration.

        - Emergency lighting units system shall be of maintained type, powered by battery/battery charger.

        - In the event of main and essential power failures to the areas served by the emergency lighting, emergency lighting shall switch on automatically and independently of the on/off mode of the normal light switch.

        - Selected lighting fixtures designated as emergency lighting fittings shall be provided as an integral part with combined battery and charging units (Battery packs).

        - On restoration of the normal supply, the fixtures shall return to the normal operating mode as they were working prior to the power interruption.

        - The battery shall be a self-contained sealed nickel cadmium pack of minimum 12V 3 Ah capacity to suit the operation of light fixtures and lamps for 3 hours continuously without any duration.

        - The charger/inverter module shall be capable of the following characteristics from a completely discharged condition:

          - Full capacity charge in 24 hours or less.

          - 60% capacity charge in 12 hours or less.

          - 30% capacity charge in 6 hours or less.

        - A LED to indicate “power supply” on shall be provided with each emergency and exit light fixture.

        - Provide fuses in the unswitched power supply and in the battery supply.

        - The changeover voltage from normal power supply to emergency shall be between 60% -85% of nominal normal voltage.

        - The battery/inverter and all circuit accessories to shall enclosed in a painted steel box.

        - All units shall have fire resisting diffusers, complying with the relevant standards and Codes of Practice mentioned elsewhere in this specification.

        - Every unit shall be connected to a permanently live supply of the local lighting circuit. Install a switch shall be installed in the permanent live supply so that regular testing can be carried out. These switches shall be situated within the unit or in the positions shown on the Drawings.

        - Illuminated exit signs shall have complied with the following:

          - All illuminated exit signs shall be fireproof and provided in accordance with BS 5588 recommendations.

          - The illuminated exit signs shall be self-contained normal/emergency exit lighting fixture, equipped with fully automatic solid state charger and sealed rechargeable nickel-cadmium battery.

          - The housing of exit light fixtures shall be made of cold rolled sheet steel, baked enamel finish, with instant-on type LED lamp/s and Arabic and English letters.  The housing shall be surface or recessed type to suit the site conditions with color of the finish as required by the Engineer.

          - Where required for normal exits and emergency fire escape routes, the illuminated exit signs shall be provided with the sign plates comprising arrow to show the direction of the exit, as approved by the Engineer.

- EXECUTION

      - INSPECTION

        - Examine the areas and conditions in which the luminaries will be installed and correct or any unsatisfactory conditions before installation commences. Do not proceed with the work until conditions have been corrected to the satisfaction of the Engineer.

        - Examine the architectural, mechanical and structural drawings and become familiar with the structural features of the building and the location of pipes, ducts, etc., which would alter the locations or spacing of outlets to the Engineer for a decision as to the proper location. This Contractor shall be responsible for the proper reinforcement of any ductwork necessary to carry the added weight of lighting fixtures where same must be mounted on the bottom of such ductwork.

      - INSTALLATION

        - Install emergency and exit lighting fixtures in accordance with the manufacturer's written instructions, applicable requirements of BS, ICE and Local Standards and with recognized industry practices to ensure that lighting fixtures fulfill requirements.

        - Furnish all fixtures complete with lamps. Emergency lighting fixtures shall be installed after completion of all masonry and structural work and shall not be used for lighting purposes during construction.

        - Where job conditions require mounting heights different from those specified or shown to avoid equipment or structural features, etc., such changes in mounting heights shall be as directed by the Engineer.

        - Lighting fixtures shall be set plumb, square, level and in alignment and shall be secured in accordance with manufacturer's directions and approved shop drawings.

      - ADJUSTMENT AND CLEANING

        - Clean all lighting fixtures of dirt and debris upon completion of the installation.

        - Protect installed fixtures from damage during remainder of construction period.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - Upon completion of installation of emergency lighting fixtures, and after building circuitry has been energized, apply electrical energy to demonstrate capability and compliance with requirements. Where possible, correct malfunctioning units at site, then retest to demonstrate compliance; otherwise, remove and replace with new units, and proceed with retesting.

        - At the time of Substantial Completion, replace lamps in lighting fixtures which are observed to be noticeably dimmed after Contractor's use and tested.

        - Test all emergency and exit lights functionally to prove that they operate satisfactorily for the intended purpose.

        - Perform actual illumination levels measurement tests for all spaces, record measurements, compare to the design requirements as per applicable standards and submit to the Engineer in schedule format for his approval.

      - EARTHING

        - Provide equipment earthing connections for all emergency and exit lights.

        - A separate earthing wire shall be used between any fixture and panel board.

- END OF SECTION