SECTION 23 3413 AXIAL HVAC FANS

| PART 1 | GENERAL |
| --- | --- |
| 1.01 SECTION INCLUDES |  |
| A. | Vane axial fans. |
| B. | Propeller fans. |
| C. | Motors and drives |
| D. | Accessories. |

- RELATED REQUIREMENTS

- Section 22 0548 - Vibration and Seismic Controls for Plumbing Piping and Equipment.

- Section 23 0513 - Common Motor Requirements for HVAC Equipment.

- Section 23 0548 - Vibration and Seismic Controls for HVAC Piping and Equipment.

- Section 23 0913 - Instrumentation and Control Devices for HVAC.

- Section 23 3300 - Air Duct Accessories: Backdraft dampers.

- Section 26 2717 - Equipment Wiring: Electrical characteristics and wiring connections.

- REFERENCE STANDARDS

- ABMA STD 9 - Load Ratings and Fatigue Life for Ball Bearings; American Bearing Manufacturers Association, Inc.; 2015.

- ABMA STD 11 - Load Ratings and Fatigue Life for Roller Bearings; American Bearing Manufacturers Association, Inc.; 2014.

- AMCA (DIR) - [Directory of] Products Licensed Under AMCA International Certified Ratings Program; Air Movement and Control Association International, Inc.; http://www.amca.org/certified/search/company.aspx.

- AMCA 99 - Standards Handbook; Air Movement and Control Association International, Inc.; 2010.

- AMCA 210 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating; Air Movement and Control Association International, Inc.; 2007 (ANSI/AMCA 210, same as ANSI/ASHRAE 51).

- AMCA 300 - Reverberant Room Method for Sound Testing of Fans; Air Movement and Control Association International, Inc.; 2014.

- AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data; Air Movement and Control Association International, Inc.; 2014.

- SMACNA (DCS) - HVAC Duct Construction Standards; Sheet Metal and Air Conditioning Contractors' National Association; 2005.

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements, for submittal procedures.

- Product Data: Provide data on axial fans and accessories including fan curves with specified operating point clearly plotted, power, RPM, sound power levels for both fan inlet and outlet at rated capacity, and electrical characteristics and connection requirements.

- Shop Drawings: Indicate assembly of axial fans and accessories including fan curves with specified operating point clearly plotted, sound power levels for both fan inlet and outlet at rated capacity, and electrical characteristics and connection requirements.

- External static pressur calculations for each fan.

- Test Reports: Indicate performance data for adjustable axial fan blades for at least five blade settings, including maximum.

- Manufacturer's Instructions: Indicate installation instructions.

- Maintenance Data: Include instructions for lubrication, motor and drive replacement, spare

parts list, and wiring diagrams.

- Maintenance Materials: Furnish the following for Employer/Owner's use in maintenance of

project.

- See Section 01 6000 - Product Requirements, for additional provisions.

- Extra Fan Belts: One set for each individual fan.

- QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in manufacturing the type of products

specified in this section, with minimum ten years of documented experience.

- DELIVERY, STORAGE, AND HANDLING

- Protect motors, shafts, and bearings from weather and construction dust.

- FIELD CONDITIONS

- Permanent fans may not be used for ventilation during construction.

PART 2 PRODUCTS

- AXIAL FANS

- Product Requirements:

- Performance Ratings: Determined in accordance with AMCA 210 and bearing the AMCA Certified Rating Seal or BS 848/BS EN ISO 5801.

- Sound Ratings: AMCA 301, tested to AMCA 300, and bearing the AMCA Certified Sound Rating Seal or BS 848.

- Fabrication: Conform to AMCA 99 or approved european equivalent.

- Performance Base: Sea level conditions.

- Temperature Limit: Maximum 149 degrees C (300 degrees F) unless otherwise stated.

- Performance:

- Values of the resistance to airflow of items of equipment, ductwork and/or the total distribution system indicated in the contract documents are approximate. It shall be the responsibility of the Contractor to verify these values based on the equipment offered and provide fans capable of delivering the required air volume when operating against the actual total system resistance. Fans shall be selected to give the air volume flow rate and achieve the noise criteria specified in the contract document.

- All fans shall be constructed to a fully developed design and shall be capable of withstanding the pressures and stresses developed during continuous operation at the selected duty. Additionally, all belt driven fans shall be capable of running continuously at 20 per cent in excess of the selected duty speed. Fan and motor assemblies shall be selected to allow a 10 percent increase in fan duty by a change of belts and pulleys only. External pressure shall increase with the "square-law", and shall be overcome.

- Hub and Impeller:

- Airfoil Impeller Blades: Adjustable die cast aluminum alloy glass reinforced polyester resin.

- Hub: Die cast aluminum alloy or cast iron hub or with belt drive of spun, welded steel, bored and keyed to shaft; to facilitate indexing of blade angle with automatic adjustment stops.

- Controllable Pitch Assemblies: Incorporate ball bearing counterbalanced blade and variable pitch assembly into hub with mechanical link to casing exterior mounted actuator, or pneumatic or electric actuator incorporated within hub.

- Cast Components: X-ray components after fabrication and statically and dynamically balance assembly before attachment to motor or shaft.

- Casing:

1. Fabricate casing of 6 mm (1/4 inch) steel for fans 1000 mm (40 inch) in diameter and smaller and 10 mm (3/8 inch) steel for larger fans.

- Continuously weld, with inlet and outlet flange connections, and motor or shaft supports. Incorporate flow straightening guide vanes for fans specified for static pressures greater than 250 Pa (one inch wg).

- Finish with one coat enamel applied to interior and exterior.

- Bearings and Drives:

- Bearings: Heavy duty pillow block type, self-aligning, grease-lubricated ball bearings, with ABMA STD 9, L-10 life at 50,000 hours.

- Shafts: Hot rolled steel, ground and polished, with keyway; protectively coated with lubricating oil.

- V-Belt Drive: Cast iron or steel sheaves, dynamically balanced, keyed. Variable and adjustable pitch sheaves for motors 15 hp and under selected so required rpm is obtained with sheaves set at mid-position; fixed sheave for 20 hp and over, matched belts, and drive rated as recommended by manufacturer or minimum 1.5 times nameplate rating of the motor.

- Belt Guard: Fabricate to SMACNA (DCS); 2.6 mm (0.106 inch) thick, 19 mm (3/4 inch) diamond mesh wire screen welded to steel angle frame or equivalent, prime coated.

Secure to fan or fan supports without short circuiting vibration isolation, with provision for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

- Lubrication: Extend lubrication fittings to outside of casing.

- Accessories:

- Guide Vanes: Welded steel construction with airfoil vanes and casing flanges, finished to match casing.

- Dampers: Welded steel construction, consisting of two semi-circular vanes pivoted on oil-retaining bearings in short casing section, finished with one coat enamel. Provide airstream operation closing blades by reverse air flow and gravity.

  - PROPELLER FANS

- Performance:

- Impeller: Shaped steel or steel reinforced aluminum blade with heavy hubs, statically and dynamically balanced, keyed and locked to shaft, directly connected to motor or provided with V-belt drive.

- Frame: One piece, square steel with die formed venturi orifice, mounting flanges and supports, with baked enamel finish.

- Accessories:

PART 3 EXECUTION

3.01 INSTALLATION

- Install in accordance with manufacturer's instructions.

- Install with vibration isolators and with flexible electrical leads; refer to Section 23 0548.

- Install flexible connections specified in Section 23 3300 between axial fan inlet and discharge ductwork. Ensure metal bands of connectors are parallel with minimum 25 mm (one inch) flex between ductwork and axial fan while running.

- Install fan restraining snubbers; refer to Section 23 0548. Adjust snubbers to prevent tension in flexible connectors when fan is operating.

- Provide backdraft dampers on discharge of exhaust fans and as indicated.

END OF SECTION