SECTION 23 3416
CENTRIFUGAL HVAC FANS

PART 1 GENERAL

- SECTION INCLUDES

- Backward inclined centrifugal fans.

- Forward curved centrifugal fans.

- Airfoil centrifugal fans.

- Tubular centrifugal fans.

- Inline centrifugal fans.

- Motors and drives.

- Fan accessories.

- RELATED REQUIREMENTS

- Section	22 0548 -	Vibration and Seismic	Controls	for Plumbing Piping and Equipment.

- Section	23 0513 -	Common Motor Requirements	for HVAC Equipment.

- Section	23 0548 -	Vibration and Seismic	Controls	for HVAC Piping and Equipment.

- Section	23 0713 -	Duct Insulation.

- Section 23 3300 - Air Duct Accessories: Backdraft dampers.

- Section 26 2717 - Equipment Wiring: Electrical characteristics and wiring connections.

- REFERENCE STANDARDS

- AMCA 210 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating; 2007.

- AMCA 300 - Reverberant Room Method for Sound Testing of Fans; 2014.

- AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data; 2014.

- AMCA 99 - Standards Handbook; 2010.

- ABMA STD 9 - Load Ratings and Fatigue Life for Ball Bearings; American Bearing Manufacturers Association, Inc.; 2015.

- ABMA STD 11 - Load Ratings and Fatigue Life for Roller Bearings; American Bearing Manufacturers Association, Inc.; 2014.

- AMCA (DIR) - [Directory of] Products Licensed Under AMCA International Certified Ratings Program; Air Movement and Control Association International, Inc.; http://www.amca.org/certified/search/company.aspx.

- AMCA 99 - Standards Handbook; Air Movement and Control Association International, Inc.; 2010.

- AMCA 210 - Laboratory Methods of Testing Fans for Certified Aerodynamic Performance Rating; Air Movement and Control Association International, Inc.; 2007 (ANSI/AMCA 210, same as ANSI/ASHRAE 51).

- AMCA 300 - Reverberant Room Method for Sound Testing of Fans; Air Movement and Control Association International, Inc.; 2014.

- AMCA 301 - Methods for Calculating Fan Sound Ratings from Laboratory Test Data; Air Movement and Control Association International, Inc.; 2014.

- SMACNA (DCS) - HVAC Duct Construction Standards; 2005.

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements, for submittal procedures.

- Product Data: Provide data on centrifugal fans and accessories including fan curves with specified operating point clearly plotted, power, RPM, sound power levels for both fan inlet and outlet at rated capacity, and electrical characteristics and connection requirements.

- Shop Drawings: Indicate assembly of centrifugal fans and accessories including fan curves with specified operating point clearly plotted, sound power levels for both fan inlet and outlet at rated capacity, and electrical characteristics and connection requirements.

- External static pressure calculations for each fan.

- Manufacturer's Instructions: Include complete installation instructions.

- Maintenance Data: Include instructions for lubrication, motor and drive replacement, spare parts list, and wiring diagrams.

- Maintenance Materials: Furnish the following for Employer/Owner's use in maintenance of project.

- See Section 01 6000 - Product Requirements, for additional provisions.

- Extra Fan Belts: One set for each individual fan.

- QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

- DELIVERY, STORAGE, AND HANDLING

- Protect motors, shafts, and bearings from weather and construction dust.

- FIELD CONDITIONS

- Permanent fans may not be used for ventilation during construction.

PART 2 PRODUCTS

- PERFORMANCE

- Product Requirements:

- Performance Ratings: Determined in accordance with AMCA 210 and bearing the AMCA Certified Rating Seal or BS 848/BS EN ISO 5801.

- Sound Ratings: AMCA 301, tested to AMCA 300, and bearing the AMCA Certified Sound Rating Seal or BS 848.

- Fabrication: Conform to AMCA 99 or approved european equivalent.

- Performance Base: Sea level conditions.

- Temperature Limit: Maximum 149 degrees C (300 degrees F) unless otherwise stated.

- Values of the resistance to airflow of items of equipment, ductwork and/or the total distribution system indicated in the contract documents are approximate. It shall be the responsibility of the Contractor to verify these values based on the equipment offered and provide fans capable of delivering the required air volume when operating against the actual total system resistance. Fans shall be selected to give the air volume flow rate and achieve the noise criteria specified in the contract document.

- All fans shall be constructed to a fully developed design and shall be capable of withstanding the pressures and stresses developed during continuous operation at the selected duty. Additionally, all belt driven fans shall be capable of running continuously at 20 per cent in excess of the selected duty speed. Fan and motor assemblies shall be selected to allow a 10 percent increase in fan duty by a change of belts and pulleys only. External pressure shall increase with the "square-law", and shall be overcome.

- WHEEL AND INLET

- Backward Inclined: Steel Galvanized construction with smooth curved inlet flange, heavy back plate, backwardly curved blades welded or riveted to flange and back plate; cast iron or cast steel hub riveted to back plate and keyed to shaft with set screws.

- Forward Curved: Galvanized steel construction with inlet flange, back plate, shallow blades with inlet and tip curved forward in direction of airflow, mechanically secured to flange and back plate; steel hub swaged to back plate and keyed to shaft with set screw.

- Airfoil Wheel: Steel construction with smooth curved inlet flange, heavy back plate die formed hollow airfoil shaped blades continuously welded at tip flange, and back plate; cast iron or cast steel hub riveted to back plate and keyed to shaft with set screws.

- HOUSING

- Heavy gage steel, spot welded for AMCA 99 Class I and II fans, and continuously welded for Class III, adequately braced, designed to minimize turbulence with spun inlet bell and shaped cut

- Factory finish before assembly to manufacturer's standard. For fans handling air downstream of humidifiers, provide two additional coats of paint. Prime coating on aluminum parts is not required.

- BEARINGS AND DRIVES

- Bearings: Heavy duty pillow block type, selfgreasing ball bearings, with ABMA STD 9 life at 100,000 hours or roller bearings, or ABMA STD 11, life at 120,000 hours.

- Shafts: Hot rolled steel, ground and polished, with keyway, protectively coated with lubricating oil, and shaft guard.

- Drive: Cast iron or steel sheaves, dynamically balanced, keyed. Variable and adjustable pitch sheaves for motors 11.2 Kw (15 hp) and under, selected so required rpm is obtained with sheaves set at mid Fixed sheave for 15 Kw (20 hp) and over, matched belts, and drive rated as recommended by manufacturer or minimum 1.5 times nameplate rating of the motor.

- Belt Guard: Fabricate to SMACNA (DCS); 2.6 mm (0.106 inch) thick, 20 mm (3/4 inch) diamond mesh wire screen welded to steel angle frame or equivalent, prime coated. Secure to fan or fan supports without short circuiting vibration isolation, with provision for adjustment of belt tension, lubrication, and use of tachometer with guard in place.

- MIXED FLOW FANS

- After fabrication all carbon steel components shall be cleaned and chemically treated by a phosphatizing process to insure proper removal of grease, oil, scale, etc. Fan shall then be coated with a minimum of 2-4 mils of Permatector (Polyester Urethane), electrostatically applied and baked. Finish color to Architect’s approval.

- Fan housing to be aerodynamically designed with high-efficiency inlet, engineered to reduce incoming air turbulence.

- Tubular fan housing shall be completely welded and coated with a minimum of 2-4 mils of Permatector (Polyester Urethane), electrostatically applied and baked. Finish color shall be to Architect’s approval. No uncoated metal fan parts will be allowed.

- Housing and bearing support shall be constructed of welded structural steel members to prevent vibration and rigidly support the shaft and bearings.

- All mixed flow housings shall include welded steel vanes to straighten airflow prior to exiting the fan discharge.

- Units shall allow for field rotation of motor positions. Units shall accommodate base mount or ceiling hung mounting without structural modifications to the fan.

- An access door shall be supplied for impeller inspection and service.

- OSHA compliant belt guard or motor cover to be included to completely cover the motor pulley and belt(s).

- Fan impeller shall be mixed flow design. The impeller shall be electronically balanced both statically and dynamically to balance grade G6.3 per ANSI S2.19.

- Fan impeller shall be manufactured with continuously welded steel airfoils and coated with a minimum of 2-4 mils of Permatector (Polyester Urethane), electrostatically applied and baked. Finish color to Architect’s approval.

- The wheel and fan inlet shall be carefully matched and shall have precise running tolerances for maximum performance and operating efficiency.

- CABINET TWIN FANS

- Fan cabinet shall house two fan centrifugal fan wheels and motors for duty and standy operation. Fan shall be equipped with sequantial timer, backdraft dampers and flow switches.

- Fan shall be compliant with all preceding clauses of the specifications.

- PERFORMANCE REQUIREMENTS

- Performance Ratings: Determined in accordance with AMCA 210 and bearing the AMCA Certified Rating Seal.

- Sound Ratings: AMCA 301, tested to AMCA 300, and bear AMCA Certified Sound Rating Seal.

- Fabrication: Conform to AMCA 99.

- Performance Base: Sea level conditions.

- Static and Dynamic Balance: Eliminate vibration or noise transmission to occupied areas.

- ACCESSORIES

- Adjustable Inlet Vanes: Steel construction with blades supported at both ends with two permanently lubricated bearings, variable mechanism out of air stream terminating in single control lever with control shaft for double width fans and locking quadrant.

- Discharge Dampers: Parallel blade heavy duty steel damper assembly with blades constructed of two plates formed around and welded to shaft, channel frame, sealed ball bearings, with blades linked out of air stream to single control lever.

PART 3 EXECUTION

3.01 INSTALLATION

- Install in accordance with manufacturer's instructions.

- Install fans with resilient mountings and flexible electrical leads. Refer to Section 23 0548.

- Install flexible connections between fan inlet and discharge ductwork; refer to Section 23 3300. Ensure metal bands of connectors are parallel with minimum 25 mm (one inch) flex between ductwork and fan while running.

- Install fan restraining snubbers; refer to Section 23 0548. Adjust snubbers to prevent tension in flexible connectors when fan is operating.

END OF SECTION