- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Fire detection system shall be intelligent device addressable, analogue detecting, low voltage and voice evacuation alarm system in full compliance with all applicable codes and standards, including, but not limited to the LOOP following:

            - Main system including all fire detection with main control panel and transponder panel.

            - Voice evacuation alarm/ notification and communication system including power amplifiers of sufficient quantities and ratings for operating all voice evacuation system speakers with 20% extra spare capacity.

            - Remote QVGA LCD Annunciators, with the same "look and feel" as the MFACP operator interface.

            - Circuit interface panels including all modules.

            - Power supplies, batteries and battery chargers of sufficient capacities for operating the system with 20% extra spare capacity.

            - Equipment enclosures.

            - Intelligent addressable manual pull stations, heat detectors, analogue smoke detectors, strobe lights both internal and external alarm monitoring modules, and supervised control modules.

            - Audible and visual evacuation devices.

            - Software and firmware as required to provide a complete functioning system.

            - Wiring and raceway.

            - Installation, testing and certification and Training.

            - Multiplex, system driven remote annunciators.

      - REFERENCES

        - Factory Mutual (FM).

        - National Fire Protection Association (NFPA):

          - NFPA 70 	National Electrical Code.

          - NFPA 72A 	Local Protective Signaling Systems.

          - NFPA 72B 	Auxiliary Protective Signaling System.

          - NFPA 72C 	Remote Station Protective Signaling System.

          - NFPA 72D 	Proprietary Protective Signaling Systems.

          - NFPA 72E 	Automatic Fire Detectors.

          - NFPA 72F 	Emergency Voice/Alarm Communication Systems.

          - NFPA 72G 	Notification Appliances for Protective Signaling Systems

          - NFPA 72H 	Testing Procedure for Protective Signaling Systems.

          - NFPA 101 	Life Safety Code.

        - Local authorities having jurisdiction (Civil Defense).

        - Underwriters Laboratories Inc.

          - UL 864		Control Units for Fire Protective Signaling Systems.

          - UL 268		Smoke Detectors for Fire Protective Signaling Systems.

          - UL 268A 	Smoke Detectors for Duct Applications.

          - UL 217	 	Smoke Detectors Single Station.

          - UL 521		Heat Detectors for Fire Protective Signaling Systems.

          - UL 228		Door Holders for Fire Protective Signaling Systems.

          - UL 464		Audible Signaling Appliances.

          - UL 1638 	Visual Signaling Appliances.

          - UL 38		Manually Activated Signaling Boxes.

          - UL 1076	Proprietary Burglary.

          - UL 346		Water flow Indicators for Fire Protective Signaling Systems.

          - UL 1481     	Power Supplies for Fire Protective Signaling Systems.

        - Local Codes and Standards.

      - SUBMITTALS

        - Include the following information in the equipment submittal:

          - Power calculations.

            - Battery capacity calculations.

            - Supervisory power requirements for all equipment.

            - Alarm power requirements for all equipment.

            - Justification showing power requirements of the system power supplies.

            - Voltage drop calculations for wiring runs in worst case condition.

          - Complete manufacturer's catalog data including supervisory power usage, alarm power usage, physical dimensions, finish and mounting requirements.

          - Submit panel configuration and interconnection of modules and all other data as required to make an informed judgment regarding product suitability. As a minimum, data shall be submitted on the following:

            - Main system including all fire detection with main and secondary control panels.

            - Circuit interface panels including all modules.

            - Power supplies, batteries and battery chargers.

            - Equipment enclosures.

            - Intelligent addressable manual pull stations, heat detectors, analog smoke detectors, alarm monitoring modules, and supervised control modules.

            - Audible and visual evacuation signals and devices.

            - Software and firmware as required to provide a complete functioning system.

            - Wiring.

            - Multiplex, system driven remote annunciators.

            - Interface module and wiring configuration from local system to Fire Command System.

          - Data describing more than one type of item shall be clearly marked to indicate the type the Contractor intends to provide for a given application. The Engineer shall assume that all options not crossed out in submitted material will be furnished for the project. Submit copies of UL listing or FM approval data showing compatibility of the proposed devices or appliances and the panels being provided.

          - Submit the following drawing for the proposed system.

            - Floor plans showing all initiating, end of line, supervisory, indicating appliances, and output control devices; including circuit interface panels, enunciators, printers, Control panel location.

            - Raceways, marked for size, conductor count with type and size, showing the percentage of allowable IEE fill used.

            - Indicate ambient sound levels used by the system layout designer for sound level calculations and mathematical justification for signal placement to meet the code required 15 dBA above ambient for audible warning signals.

            - Wiring diagrams showing points of connection and terminals used for all electrical connections to the system devices and panels.

            - Complete single-line riser diagram showing all equipment and the size type and number of all conductors.

          - Submit Method Statement for system’s component wiring, installation, testing, commissioning and operating.

          - All civil, MEP and support works, including and not limited to:

            - Containment.

            - Cabling.

            - Scaffolding and access ladders.

            - Labor.

            - Power supply.

            - Other tools & services.

          - Unless advised otherwise, contractor is self-supportive and should include for his offer his own materials, tool, services, office, and any requirement necessary to complete this project.

          - Provide samples of each type of proposed systems’ devices; detectors, speakers, flashers, sirens, horns, manual call points, fire resistant wiring, fittings, accessories, ..etc together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

          - Coordination with other parties.

            - Method statement.

            - Scope of work matrix for all works listed in this Contract Deliverables Section.

            - Communication protocol.

          - Outline risk assessment for all major aspects of the works.

          - General method statement/risk assessment on approach to day to day responsibilities.

          - List of Spare parts to be provided for minimum 10 years.

          - Item by Item commentary on technical requirements.

          - The Contractor shall comply with all specifications described in the Technical Specification sections herein. System specifications proposed should reflect each of the system components in question, functionality desired by the system component and the how the component integrates with the centralized system. The contractor shall add 3 columns beside each item to state the following:

            - First column is ‘Bidder’s Compliance’: Contractor shall specify here one of the below:

              - Y: proposal does comply with specification/requirement.

              - N: proposal does not comply with specification/requirement.

              - N/F: proposal does not fully comply with specification/requirement.

              - N/A: specification/requirement is not applicable to the project.

            - Second column is ‘Reference’:

              - Contractor shall refer each compliant item to the related section of proposal, such as PA system.

              - Component data sheet or reflected electrical/ceiling/wall plans layout drawing.

            - Third column is ‘Bidder’s Comments’:

              - Contractor shall note down any further description, comment, feedback, concern, etc. on each item.

              - Contractor shall note down any further description, comment, feedback, concern, etc on each item.

          - Vendor certificates.

            - Company certification by vendor as authorized dealer.

            - Personnel certificate by vendor as factory-trained.

            - Product quality assurance certification by vendor.

          - Vendor list and selection criteria for all items, vendors should adhere to the following criteria:

            - Company established at least 10 years ago.

            - Have references of at least 20 projects globally of similar scope & complexity.

            - Based in Sudan since at least 5 years.

            - Have references of at least 5 projects in Sudan of similar scope & complexity.

            - Have a local support office.

            - Have a local warehouse for spare parts stocking.

          - Proposed subcontractors identified and scope of work for each.

          - Confirmation of guarantee periods for equipment and guarantee terms & conditions.

          - Confirmation of warranty periods for equipment and guarantee terms & conditions.

          - Maintenance & support offering – sufficient details.

          - Other supporting information that adds value to the proposal.

        - Bidder’s Compliance Letters.

          - Conformity of bid to requirements – sufficient technical details.

          - Conformity to agree on Confidentiality Agreement.

          - Letter of Bidder’s Compliance with All Specifications.

          - Conformity of responsibility to secure Compliance with related government/utility authority.

        - List of Proposed Personnel with CVs & Responsibility Matrix.

          - Relevant experience for key team members.

          - Other supporting information that adds value to the proposal.

        - Schedule of Works: Bidder shall compile a schedule of works and include a project milestone as per Master Schedule of Works provided. It is up to the bidder to create a schedule that best incorporates all works.

        - Handover & Close-Out Documentation.

          - As Built Drawings.

          - End User Manuals.

          - Maintenance Manual.

          - Operations Manual.

          - Plans as mentioned above.

          - S/W license, update and upgrade .procedures.

          - Other supporting information that adds value to the proposal.

        - Submit complete system detailed dimensional workshop layouts and single line diagrams (system risers) drawings approved, signed and stamped from the local fire authority prior to any material ordering or system installation.

        - Submit from the system Supplier full detailed calculation of system power supplies, voltage drops, on devices wiring circuits, amplifiers sizing,..etc.

      - CLOSEOUT SUBMITTALS

        - Requirements of Division 01.

        - Project Record Documents: Record actual locations of busway routing and location of plug-in units.

        - Operation and Maintenance Data: Submit joint re-tightening schedule.

      - QUALIFICATION

        - Manufacturer: Firms regularly engaged in the manufacturing and sale of analogue fire detection devices for a period exceeding ten years. The manufacturer shall have an installed base of analogue systems as a reference. The Contractor shall contract with a single source for supplying job materials, services, and programming, including final inspection/test services for the fire alarm system.

        - Installer: Firms regularly engaged and qualified in installing fire alarm and detection systems of the same type and design as specified. Include the names and locations of at least two such installations, specify type and design for each system and furnish documentation that the system has performed satisfactorily for the preceding 18 months.

        - Contractor Qualification

        - Manufacturer Qualification

      - QUALITY ASSURANCE

        - Provide the services of a representative or technician from the manufacturer of the system, experienced in the installation and operation of the type of system provided. The technician shall supervise installation, software documentation, adjustment, preliminary testing, final testing and certification of the system. The technician shall provide the required training to the Owner's personnel in the system operation, maintenance and programming.

        - The Contractor through the system’s supplier/ installer shall verify and confirm that the designed system fulfill all local codes and Civil Defense requirements, otherwise he shall inform the Engineer about any incompliance or further required action prior to installation of the system. The Contractor shall bear all the responsibility of getting Civil Defense approval for the installed system.

      - PRE-INSTALLATION MEETINGS

        - Convene minimum one week prior to commencing work of this section.

      - DELIVERY, STORAGE, AND HANDLING

        - Protect from moisture by using appropriate coverings. Store in dry interior locations.

      - SEQUENCING

        - Sequence Work to avoid interferences with building finishes and installation of other products.

      - OPERATIONS AND MAINTENANCE DATA

        - Complete operation and maintenance manual with two sets of proposed installation drawings shall be submitted.

      - SPARE PARTS

        - Furnish extra materials described below that match product installed and that are packaged with protective covering for storage and identified with labels describing contents.

        - Lamps for Remote Indicating Lamp Units: Quantity equal to 2 percent of amount installed, but not less than one unit.

        - Lamps for Strobe Units: Quantity equal to 2 percent of amount installed, but not less than one unit.

        - Smoke Detectors, Beam detectors, Heat Detectors, Control element, Master element and Manual Stations: Quantity equal to 2 percent of amount of each type installed, but not less than one unit of each type.

        - Detector Bases: Quantity equal to 1 percent of amount of each type installed, but not less than one unit of each type.

        - Loudspeakers, Fire speaker, Horns: Quantity equal to 2 percent of amount of each type installed, but not less than 1 unit of each type.

        - Fire telephone jacks, Fireman microphones and speakers, etc units: Quantity equal to 5 of each type installed.

        - Loop cards: 2% with a minimum of one piece.

        - Printer Ribbons: Six spares.

        - Keys and Tools: One extra set for access to locked and tamper-proofed
components.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Three Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and software and hardware administration of the system without or with minimal assistance from the vendor’s technical staff.

      - DESCRIPTION OF SYSTEM

        - Supervised pre-signal annunciated closed circuit 24 volt ac/dc system.

        - Provide main fire alarm panel , Transponder fire alarm panel, repeater panels, controllers, power supply unit for each panel of sufficient capacity for operating the system with 20% extra spare capacity, manual call stations, heat detectors, smoke detectors, sounders, strobes, initiating and indicating device circuits, fully supervised as shown on the drawings.

        - Provide voice evacuation system for alarm notification as part of the main & Transponder fire alarm control panels. The voice evacuation system shall include amplifiers of sufficient quantities and ratings for operating all voice evacuation system speakers with 20% extra spare capacity, zoning, controllers, speakers... etc.

        - Provide a remote QVGA LCD Annunciators, with the same "look and feel" as the FACP operator interface. The Remote QVGA LCD Annunciator shall use the same Primary Acknowledge, Silence, and Reset Keys as the FACP.  The repeater panel is wired directly from the main F.A.

        - Provide all needed power supplies for the full capacity operation of the system with addition 20% extra spare capacity, any extra needed power supplies due to any wiring rerouting, are included in price of the fire alarm system.

        - System to operate with manual stations and detectors, circuits as follows:

          - Actuate control panel to cause alarm signal continuously throughout building.

          - Indicate alarm origin on the F.A. panels/and the repeater panels.

          - Shutdown air conditioning where specified.

          - Start pressurization and smoke extract management system where specified

          - Shutdown any combustible gas supplies to kitchen.

          - Indicate origin of signal.

          - Send signal to elevators to act as programmed during fire cases.

          - Send signal to access control panel to release all strikes at accesses within fire zone.

        - Electromagnetic Compatibility

          - All equipment and systems installed under this Contract shall meet following specifications on electromagnetic compatibility:

            - Interference immunity according to BS EN 61000: Part 6-3.

            - Emitted interference according to BS EN 61000: Part 6-2.

- PRODUCTS

      - GENERAL EQUIPMENT AND MATERIAL REQUIREMENTS

        - All equipment shall be new and unused.  All components and systems shall be designed for uninterrupted duty. All equipment, materials, accessories, devices, and other facilities covered by this Specification or shown on the Drawings and installation specifications shall be the best suited for the intended or if provided by different manufacturer, recognized as compatible by both manufacturers.

        - Service availability: The supplier shall have sufficient stock on hand and have a fully equipped service organization capable of guaranteeing response time within 8 hours of service calls, 24 hours a day, 7 days a week to service completed systems.

      - CONTROL PANEL

        - Provide analogue addressable Main fire alarm control panel and transponder panel with capacities as shown on drawings with two additional spare loops for each panel, the loop should take 250 Devices. The panels shall be expandable to two additional loops. Each loop shall be capable of driving the number of analogue addressable devices as shown on the drawings.

        - Provide a remote QVGA LCD Repeater Panels, with the same "look and feel" as the main FACP operator interface. Each Remote Repeater Panel shall use the same Primary Acknowledge, Silence, and Reset Keys as the Main FACP.  The repeater panel is wired directly from the main FACP.

        - Provide auto dialer as shown on the drawings, the auto dialer shall have the capability to store a minimum of one digitally encoded message and four telephone numbers.  The unit shall be programmed to dial all stored numbers until one answer the call, the unit shall be triggered by means of fire condition.

        - Main Fire Alarm Control Panel

          - The control panel shall be UL/FM approved.

          - The control panel shall be capable of receiving and analyzing signals from fire detectors, providing audible and visual information to the user and initiating automatic alarm response sequences.

          - It shall monitor and repeat events in transponder panel/s.

          - The panel shall have all required interface modules/units to connect to the BMS for status only.

          - It shall be modular in construction allowing for future extension of the system and shall be able to be easily configured to meet the exact detection zone and output-mapping requirements of the areas considered and be microprocessor-based operating under a multi-tasking software program. Operating programs and configuration data must be contained in easily up-datable non-volatile memory (EPROM).

          - It shall incorporate a real time clock to enable events to be accurately referenced against time and date.

          - The panel must have redundant master controller (CPU), In case the first master controller (CPU) fails, the system will automatically switch to the second master controller (CPU) (Hot Swap). The system will stay fully function as it was programmed.

          - The panel shall incorporate a key switch to prevent unauthorized use of the manual controls.

          - The panel shall be capable of operating with analogue addressable detectors and addressable ancillary equipment.

          - Provision shall be made for each addressable loop to be sub-divided into geographical zones. The section of wiring corresponding to each zone circuit shall be protected from faults in other sections by line isolator modules.

          - In order to facilitate re-configuration and system extension, the allocation of addresses to devices shall be independent of their physical arrangement on the loops.

          - The panel shall have provision to house the AC Main power supply and batteries.

          - The panel shall monitor the status of all devices on the addressable loops for fire, short-circuit fault, open-circuit fault, incorrect addressing, unauthorized device removal or exchange, pre alarm condition and contaminated sensor condition.

          - All internal connection and interfaces including charger, battery and remote signaling functions shall also be monitored.

          - The panel shall communicate with the BMS thru auxiliary relay for general status monitoring.

          - The panels shall have an integral alphanumeric display and system controls: include a 700 character, expanded content multi-line qvga lcd display to indicate alarm, supervisory, and component status messages and shall include a keypad for use in expanded content, multi-line operator interfaces shall be capable of providing the following functions:

          - Dual language operation with Instant-Switch language selection during runtime.

          - Activity display choices for:

            - First 8 Events.

            - First 5 Events and Most Recent Event (with first and most recent event time and date stamps).

            - First Event and Most Recent Event (with first and most recent event time and date stamps).

            - Scrollable List Display displays a scrollable list of active points for the event category (alarm, priority 2, supervisory, or trouble) selected. The position in this list will be the last acknowledged point (not flashing) at the top followed by the next 7 unacknowledged points (flashing).

            - General Event Status (alarm, priority 2, supervisory, or trouble in system)

            - Site Plan

            - Equal or hierarchal priority assignment. In systems with two or more operator interfaces, each operator interface shall be programmable to allow multiple operator interfaces to have equal operation priority or to allow hierarchal priority control to be assigned to individual operator interfaces (locations).

            - Up to 50 custom point detail messages for providing additional point specific information in detailed point status screens.

            - Bitmap file import for operator interface display of site plan and background watermark images. Site plan status icons shall indicate area status for highest priority active events.

          - The panel shall be capable of monitoring and controlling remote devices, such as relays for the control mechanical equipment directly from the addressable loops.

          - The panel shall interrogate each addressable device at least once every 4 seconds and shall incorporate fire decision specifically adapted to the response characteristic of the analogue addressable detectors employed.

          - The circuitry shall be designed so that, for each type of analogue addressable detectors the overall response time including the detector, the signal transmission system and the fire decision algorithm, meets the requirement of the relevant part of NFPA 72.

          - A facility must be provided to automatically adjust the sensitivity of analogue detectors to a higher level for periods of time when the building is unoccupied shall be provided.

          - The panel shall have the ability to annunciate a pre-alarm condition designed to give the earliest possible warning of a potential fire condition without raising the full alarm condition.

          - The panel shall have the ability to automatically adjust the alarm and pre-alarm threshold levels to compensate for changes in detector sensitivity due to contamination over a period of time.

          - The panel shall have the ability to provide automatic warning that a detector has reached a level of contamination, which requires that it be replaced or serviced.

          - The panel shall be capable of generating customer definable time delay sequences to upgrade, without the need for external timers, alarm sounder responses as follows:

            - Silent to Alert

            - Alert to Evacuate

            - Silent to user defined tone

          - The panel shall monitor all critical system components and interconnections, internal and external, such that failure, which would prevent the correct operation of the alarm functions, causes the FAULT indicator to light and a message to be given on the alphanumeric display.

            - The following faults shall be reported:

              - Loop Short Circuit

              - Loop Open Circuit

              - Un configured Device

              - Addressable Device Failure

              - Device Not Responding

              - Incorrectly Configured Device

              - Detector Condition Monitoring Device

              - Detector Circuit Wiring Fault

              - Repeater / Repeater LCD, Remote Printer Failure

              - Power Supply Unit Fault

              - Charger Fault

              - Battery Fault

              - Battery Critical

              - Mains Failure

              - Relay Output Stuck

              - Signaling Fault

              - Sounder Wiring Open Circuit

              - Sounder Wiring Short Circuit

          - The panel shall provide text messages to indicate the location of where a fault has occurred in the system.

          - The panel shall incorporate the following system management facilities:

            - Isolate/re-connect a particular addressable point

            - Isolate/re-connect a particular detector zone

            - View the number of alarms  since power up

            - View the number of software initialization since power up

            - View common alarm status

            - View common fault status

            - View common disabled status

            - View zone alarm status

            - View zone fault status

            - View zone isolated status

            - View point address status

            - Print event log

            - Print points isolated

            - Print points in detector Condition Monitoring Fault

            - Print point status

          - The panels shall have an event log capable of storing 1200 events min that have occurred. It shall be possible to view the content of the log via the alphanumeric display.

          - Events shall be displayed in chronological order in any of the following three options:

          - Newest event first

          - Oldest event first

          - Highest priority event first

          - The panel shall be capable or providing audible and visual warning when a weekly system test.

          - The panel shall be with 2 GB Compact Flash memory, and with Ethernet built in ready connectivity.

      - POWER SUPPLIES

        - The Power Supply /Batteries/Charger, shall provide the means of automatically supplying 24 V DC operating and emergency power to the system.  The power supply shall be capable of powering Notification appliance circuits shown on drawings with 20% spare capacity. The power supply shall be a minimum of 80% efficient, fully regulated, power limited 24 V DC to operate listed signaling devices. The power supply shall provide diagnostic LED’s to notify the operator upon AC power and/or the control panel battery detection, system ground fault detection when connected to the control unit and shall be capable of charging from 5 AH to 50 AH batteries.  Upon AC power failure the power supply shall automatically transfer the system to battery backup and battery shall be heavy duty higher performance with sufficient capacity to maintain the system for 24 hours followed by an alarm condition for 30 minutes.

        - Features

          - High Efficiency Design.

          - Completely Power Limited.

          - 100% Fully Regulated Power Supply.

          - Primary Power (AC) Monitor.

          - Automatic Battery Charger Circuit.

          - Dual 3 Amp Output with Electronic Current Limiting min.

          - Ground Fault Detection Circuit.

          - Battery Monitor Circuit; Hi/Lo Voltage and Open.

          - 5-50 AH Battery Charging Capacity.

          - Sealed lead-acid

          - Where required provide Intelligent Remote Battery Charger for charging up to 110Ah batteries

      - INTELLIGENT PERIPHERAL REQUIREMENTS

        - Provide intelligent analogue smoke and thermal sensors as shown. All intelligent sensors, shall communicate with the control panel over fire resistance 2 wires cable. The address shall be dialed in at the sensor by the installer using the rotary switches located in the sensor head or module.  All intelligent analogue sensors shall be interchangeable, ceiling mountable and shall use common twist-lock bases.

          - Intelligent Photoelectric Sensor:

            - The Intelligent Photoelectric Sensor shall connect with fire resistance 2 wires to the control panel.  The sensor shall be easy to install into the base. The sensor shall incorporate a built in type identification so the system can identify the type of sensor.  The sensor shall be continually monitored to measure any change in their sensitivity because of the environment (dirt, smoke, temperature, humidity, etc.).  The sensor shall use the photoelectric principle to measure smoke density and shall on command from the control panel send data to the panel representing the analog value of the smoke density.  The sensor shall provide advanced indication of the analog value of the level of smoke density to the panel that maintenance is required, reducing the maintenance required to inspect routinely all sensors in order to ensure normal operation.  The sensors shall have 8 selectable sensitivity levels ranging from 0.5% to 3.7%, programmed and monitored from the FACP.

          - Intelligent Photoelectric Sensor with Sounder Base: NA

            - Shall have all specs as intelligent photoelectric sensor above, but with built in electronic alarm sounder.

            - Piezoelectric sounder provides high output (88dBA) with low current requirements (20 mA).

          - Intelligent Thermal/Heat Sensor:

            - The Intelligent Analog Thermal/Heat Sensor shall connect with fire resistance 2 wire to the control panel.  The sensor shall be easy to install into the base.  The sensor shall incorporate a built in type identification so the system can identify the type of sensor.  The sensor shall be continually monitored to measure any change in their sensitivity, because of the environment (dirt, temperature, humidity, etc.).  The sensor shall use dual solid state to monitor rate of heat rise in accordance to NFPA 72 Temperature Classification for Ordinary Temperature Rating Range (58 – 79°C) and provide a fast response to rapid increases in temperature.  The sensor on command from the control panel, shall send data to the panel representing the analogue value of the ambient temperature.

          - Intelligent Dual-Sensor Smoke/ Heat  Detector:

            - The Intelligent Dual-Sensor Smoke/ Heat Detector shall connect with fire resistance 2 wires to the control panel.  The detector shall contain photoelectric sensor with integral thermal sensor. The detector shall incorporate a built in type identification so the system can identify the type of sensor. The Detector shall be continually monitored to measure any change in their sensitivity because of the environment (dirt, smoke, temperature, humidity, etc.).  The sensor shall provide advanced indication of the analog value of the level of smoke density to the panel that maintenance is required, reducing the maintenance required to inspect routinely all sensors in order to ensure normal operation.

            - Smoke sensor sensitivity Range: 0.2% to 3.7% per foot of smoke obstruction, selected at control panel.

            - Smoke sensor air velocity range: 0-1220m/min.

            - Thermal sensor operation (selected at control panel): fixed alarm temperature setting of 57.2 C deg, and/ or rate of rise temp. alarm at 8.3C deg or 11.1 C deg, also selectable as utility monitoring operation from 0 to 50C deg.

          - Intelligent Monitor Module:

            - The Intelligent Monitor Module shall be used to connect a supervised conventional initiating device or zone of supervised conventional initiating devices (water flow switches, tamper switches, manual pull stations 4 wire smoke detectors conventional 4 wire duct/plenum detectors, etc. to one of the 2 wire intelligent analog loop cards.  The module shall mount in an electrical box and shall be capable of Class "A" supervised wiring to the initiating device.  In order to maintain proper supervision there shall be no T-taps allowed on Class "A" lines.  The Monitor Module shall provide internal identifying code which the control panel shall use to identify the type of device.  The Monitor Module shall contain an integral LED that flashes each time the monitor module is polled.

          - Intelligent Sound & Control Modules:

            - The Intelligent Sound & Control Modules shall be used to connect and supervise conventional indicating device or zone of indicating devices that require an external power supply, such as horns, strobes, A/Vs, to one of the 2 wire intelligent analog loop (Class “A”).  The control Module shall be capable of operating as a relay (dry contact form C), to control Door Holders, Air Handling units etc.  The module shall mount in an electrical box and shall be capable of Class "A" supervised wiring to the indicating or control device.  The Control Module shall provide an internal identifying code which the control panel shall use to identify the type of device.

          - Isolating Module:

            - The Isolating Module shall be an automatic switch, which will open when the intelligent loop voltage drops below 4 Volts.  The Isolator Module shall be placed between groups of sensors/intelligent modules on the loop in order to protect the intelligent loop if a short should occur.  If a short occurs between any two isolators, then both isolators switch to open circuit conditions and isolate the group of sensors/modules between them.  The remaining devices on the intelligent loop shall continue to operate and communicate normally.  The number of devices between isolators shall be as recommended by manufacturer or less.  The Isolator shall be designed to mount in an electrical box.

          - Door Hold Units

            - Door hold units shall be 24 V.D.C. fail safe type and shall be integral with the floor spring of the door.

            - Final electrical connections shall be made using heat resisting flexible cable from a flex outlet plate located as close as practical to the door loaded unit.

            - A door release push button connected in series with the door release coil shall be provided adjacent to each door or pair of doors fitted with door hold units. The button shall be mounted at 1350 mm A.F.F.L. and engraved "Door Close".

            - A separate 24 V.D.C. power supply shall be provided to serve the door hold units and the release signals shall be provided via relays operated from the fire alarm system.

          - Door release Unit

            - Where doors are normally kept locked for security purposes provision shall be made for these to be released when a fire alarm signal is raised. The release circuits shall be related to the loop and adjacent loops in which an alarm originates.

            - The release mechanism shall comprise a brass keep fitted into the doorframe and related to the door lock. Upon signal from the fire alarm system, a solenoid shall release the lock allowing the door to open.

          - Duct Mounted Smoke Detector

            - NFPA 72E, ionization type with auxiliary SPDT relay contact, key-operated NORMAL-RESET-TEST switch, duct sampling tubes extending width of duct, and visual indication of detector actuation, in duct-mounted housing. Addressable analogue type.

          - VOICE EVACUATION

            - General: Comply with UL 864, "Control Units for Fire-Protective Signaling Systems", and NFPA 72.

            - Voice Alarm: Provide an emergency communication system, integral with the MFACP, and transponder panel including voice alarm system components, microphones, amplifiers, and tone generators. Features include:

              - Amplifiers comply with UL 1711, "Amplifiers for Fire Protective Signaling Systems." Amplifiers shall provide an onboard local mode temporal coded horn tone as a default backup tone. Test switches on the amplifier shall be provided to test and observe amplifier backup switchover. Each amplifier shall communicate to the host panel amplifier and Notification Appliance Circuits (NAC) circuit voltage and current levels for display on the user interface. Each amplifier shall be capable of performing constant supervision for non-alarm audio functions.

              - The amplifiers shall be of sufficient quantities and ratings for operating all voice evacuation system speakers with 10% extra spare capacity.

              - Eight channel multiplexed audio for systems that require more than two channels of simultaneous audio. Up to 8 channels of audio shall be multiplexed on Class A fire resistant cable.

              - Emergency voice communication audio controller module shall provide up to 30 minutes of memory stored messages. Provide supervised connections for master microphone and up to 10 remote microphones.

              - Status annunciator indicating the status of the various voice alarm speaker zones and the status of fire fighter telephone two-way communication zones.

            - Distributed Module Operation: MFACP and transponder panel shall be capable of allowing remote location of the following modules; interface of such modules shall be through a Class A fire resistant UTP cable supervised serial communications channel (SLC):

              - Amplifiers, voice and telephone control circuits

              - Notification Appliance Circuits

      - ALARM UNITS

        - Audible Alarm Notification: By voice evacuation and tone signals on loudspeakers in areas as indicated on drawings.

          - Automatic Voice Evacuation Sequence:

            - The audio alarm signal shall consist of an alarm tone for a maximum of five seconds followed by an automatic voice message. At the end of the voice message, the alarm tone shall resume. This sequence shall sound continuously until the "Alarm Silence" switch is activated.

            - All audio operations shall be activated by the system software so that any required future changes can be facilitated by authorized personnel without any component rewiring or hardware additions.

        - Ceiling Speaker: Speaker notification appliances shall be listed to UL 1480.

          - The speaker shall operate on a standard 25VRMS or 70 VRMS Notification Appliances Circuits (NAC) using fire resistant unshielded twisted pairs (UTP) cables.

          - Voice alarm speakers shall be with multi tapping including 2W, 1 W, 1/2 w, 1/4w and shall produce a sound level at least 15dB above the reduced average ambient sound level or 5dB above the maximum sound level having a duration of at least 60 seconds measured at 1.5m above the floor.

          - The speaker shall have a frequency response of 400 to 4000 Hz for Fire Alarm and 125 to 20 kHz for General Signaling.

        - Horn Loudspeaker

          - A supervised horn loudspeaker equipped with a compression driver providing up to 15 Watts RMS power handling capability, superior intelligibility and dispersion to achieve maximum sound projection and penetration.

          - Weather-resistant, vandal-resistant aluminum construction assures protection against water, humidity, vermin, and corrosion

          - With wall mounting bracket which allows directional sound dispersion via vertical and horizontal positioning.

          - Including a built-in 25/70/100 V transformer featuring a screwdriver adjustable, 7-position watt/impedance selection switch. Wiring terminals are protected with a vandal-resistant adapter cover for control equipment utilizing cable or conduit.

          - Shall meet or exceed the UL Listed standards for audible signal appliances and are capable of operating within an ambient temperature range of 66°C (150°F) to -35°C (-30°F).

          - Shall comply with UL Standard 1480 — Speakers for Fire Protective Signaling Systems.

          - With 5 mfd Capacitor for Line Supervision

          - With reentrant acoustic path.

          - With red baked epoxy finish.

          - Installation terminals and power selector are recessed mounted, and protected by the metal interface adapter, or clear plastic shield.

          - Specifications (UL Rating):

            - Power rating: 15W continuous

            - Frequency Response: 400-14,000Hz (Nominal).

            - Sensitivity: 102 dB @ 15 Watts @ 3m

            - Dispersion angle: 70 Degrees (-6 dB @ 2,000 Hz Octave Band).

        - Visible/only multi candela: strobe shall be listed to UL 1971. The V/O shall consist of a xenon flash tube and associated lens/reflector system. The V/O enclosure shall mount directly to standard single gang, double gang or 4" square electrical box, without the use of special adapters or trim rings.  V/O appliances shall be provided with different minimum flash intensities of 15cd, 30cd, 75cd and 110cd.  Provide a label inside the strobe lens to indicate the listed candela rating of the specific visible/only appliance.

        - Audible/visible multi candela: audible/visible (A/V) notification appliances shall be listed to UL 1971 and UL 464. The strobe light shall consist of a xenon flash tube and associated lens/reflector system. Provide a label inside the strobe lens to indicate the listed candela rating of the specific strobe. The strobe shall be provided with different minimum flash intensities of 15cd, 30cd, 75cd and 110cd. The horn shall have a minimum sound pressure level of 83 or 89 dBA @ 24vdc. The audible/visible enclosure shall mount directly to standard single gang, double gang or 4" square electrical box, without the use of special adapters or trim rings.The audible/visible enclosure shall mount directly to standard single gang, double gang or 4" square electrical box, without the use of special adapters or trim rings. The appliance shall be capable of two-wire synchronization with one of the following options:

          - Synchronized Strobe with Horn on steady.

          - Synchronized Strobe with Temporal Code Pattern on Horn.

          - Synchronized Strobe with March Time cadence on Horn.

          - Synchronized Strobe firing to NAC sync signal with Horn silenced.

        - Accessories: the contractor shall furnish the necessary accessories.

        - Deaf Alarm System:

          - Deaf alarm control panel with strobe and bed vibrator with the option to add a second vibrator or strobe.

          - Suitable for connection into a 24Volt commercial fire alarm system through addressable interface control module.

          - With built in battery backup.

          - The control unit is powered from an external 240V, 50Hz power supply.

          - Complies with BS 5446-1:1990

          - Continuous monitoring of cables

          - Test buttons for strobe, vibration pad, sensor and system

          - Temperature range: 0 to 40 C Deg.

          - Humidity range: 0% to 90% relative humidity.

      - PERIPHERAL EQUIPMENT

        - MANUAL PULL STATION:

          - Provide addressable manual pull station as shown, the double action manual station shall be push and pull type switch.  The manual station, should be made of red lexan, with molded, raised-letter operating instructions of contrasting color. Station will mechanically latch upon operation and remain so until manually reset by opening with a key common with the control units.  The manual station shall mount to a standard single gang switch box or an optional red surface mount box.

      - WIRING OF SYSTEM

        - Fire alarm wiring shall be completely segregated from any other system.

        - All cables associated with the fire alarm installation shall be fire resistant copper cables as described in this specification with a red PVC oversheath.

        - All wiring shall be carried out using fire resistant for 60 minutes minimum, zero halogen, low smoke and flame sheathed according to IEC 60332. Joints in cables shall be made only at accessories unless otherwise agreed with the Engineer when the joint box shall be detailed on record drawings.

        - Fire detectors and devices and Alarm notification devises shall all be connected on a two wire fully maintained closed circuit (Class A).

        - Fire alarm cables shall be installed in galvanized steel conduits concealed in the building fabric except in plant rooms and service where a surface installation shall be provided.

        - Connection between main control panel and transponder panel shall be through SWA armoured cable fire resistant for 60 minutes.

        - Fire resistant cables shall be third party approved by LPCB complying to the following:

          - BS 7629: Part 1: 1997 – 300/500 V fire resistant electrical cables having low emission of smoke and corrosive gases when affected by fire – Multicore cables.

          - Standard fire resistant cables as described in clause 26.2d of BS 5839-1:2002 – Fire detection and alarm systems for buildings. Code of practice for system design, installation, commissioning and maintenance,

          - Class PH30 when tested in accordance with BS EN 50200: 2000 – Method of test for resistance to fire of unprotected small cables for use in emergency circuits.

        - Fire resistant cables construction shall include:

          - Conductors: Plain annealed copper to BS 6360 solid (class 1).

          - Insulation: High performance silicon rubber EL2 to BS 7655: section 1.1

          - Earth Conductor: Tinned annealed copper to BS 6360

          - Electrostatic Screen: Aluminum/polyester tape 125% coverage

          - Sheath: Thermoplastic zero halogen, flame retardant, abrasion resistant type LTS3 to BS 7655: SECTION 6:1.

- EXECUTION

      - INSTALLATION DRAWINGS

        - Show a general layout of the complete system including equipment arrangement specific to the equipment manufacturer’s requirements. It shall be the responsibility of the Contractor to verify dimensions and assure compatibility of all other systems interfacing with the fire alarm system.

          - Identify on the drawings, conduit and conductor sizes and types with number of conductors in each conduit. Provide each conduit and device with a unique identification. For addressable alarm initiation devices, the system identifier shall be the system address for that device. Signals shall be sequentially numbered as the address of the controlling module.

          - Indicate on the point to point wiring diagrams, interconnecting wiring within the panel between modules, and connecting wiring to the field device terminals.

          - Provide mounting details of FACPs and other boxes to building structure, showing fastener type, sizes, material and embedded depth where applicable.

        - The Contractor through the system’s supplier/ installer shall verify and confirm that the designed system fulfill all local codes and Civil Defense requirements, otherwise he shall inform the Engineer about any incompliance or further required action prior to installation of the system. The Contractor shall bear all the responsibility of getting Civil Defense approval for the installed system.

      - INSTALLATION

        - Perform work in accordance with the requirements of NFPA 70 and NFPA 72 (A to G).

        - Fasten equipment to structural members of building or metal supports attached to structure, or to concrete surfaces.

          - Use clamping devices for attaching to structural steel, or when clamping is impractical, obtain written authority to weld or to drill.

          - Fasten equipment to concrete or masonry with expansion anchors.

          - Fasten equipment to drywall by screws into studs, and to metal wall panels by weld studs, bolts or self-taping metal screws.

          - Do not install conduit raceways and boxes in positions that interfere with the work of other trades.

          - Attach nameplates on panels or other components as specified.

          - Cable types, method of installation and circuit identification shall be in accordance with the manufacturer’s requirements.

      - DEVICES

        - Relays and other devices to be mounted in auxiliary panels are to be securely fastened to avoid false indications and failures due to shock or vibration.

        - Wiring within panels shall be arranged and routed to allow accessibility to equipment for adjustment and maintenance.

        - Detectors shall be installed in accordance with NFPA 72.  Detectors shall be at least 300 mm from any part of any lighting fixture. Detectors shall be located at least 900 mm from diffusers of air handling systems. Each detector shall be provided with appropriate mounting hardware as required by its mounting location. Detectors which mount in free space shall be mounted directly to the end of the stubbed down rigid conduit drop.  Conduit drops shall be firmly secured to minimize detector sway.  Where length of conduit drop from ceiling or wall surface exceeds 900 mm, sway bracing shall be provided.

        - Notification appliances shall be mounted a minimum of 2.4 m above the finished floor unless limited by ceiling height or otherwise indicated.

        - Annunciator equipment provided shall be mounted where indicated.

        - Devices exposed to external weather shall be of special type they shall be protected against humidity and off shore weather condition.

      - SPLICES AND CABLE TERMINATIONS

        - All splices shall be made using solder less connectors or compression type terminal strips. All connectors shall be installed in conformance with the manufacturer’s recommendations.

        - Crimp-on type spade lugs shall be used for terminations of stranded conductors to binder screw or stud type terminals. Spade lugs shall have upset legs and insulation sleeves sized for the conductors.

      - CERTIFICATE OF COMPLIANCE

        - Complete and submit to the Engineer in accordance with NFPA 72, paragraph 2.2.2, and in full compliance with Civil Defense requirements.

      - FIELD QUALITY CONTROL

        - Testing, general:

          - All intelligent analog devices shall be tested for correct address and sensitivity using test equipment specifically designed for that purpose. These devices and their bases shall be tagged with adhesive tags located in an area not visible when installed, showing the system address, initials of the installing technician and date.

          - Wiring runs shall be tested for continuity, short circuits and grounds before system is energized. Resistance, current and voltage readings shall be made as work progresses.

            - A systematic record shall be maintained of all readings using schedules or charts of tests and measurements. Areas shall be provided on the logging form for readings, dates and witnesses.

            - The acceptance inspector shall be notified before the start of the required tests. All items found at variance with the drawings or this specification during testing or inspection by the acceptance inspector, shall be corrected.

            - Test reports shall be delivered to the acceptance inspector as completed.

          - All test equipment, instruments, tools and labor required to conduct the system tests shall be made available by the installing contractor. The following equipment shall be a minimum for conducting the tests:

            - Ladders and scaffolds as required to access all installed equipment.

            - Multimeter for reading voltage current and resistance.

            - Intelligent device programmer/tester.

            - Laptop computer with programming software for any required program revisions.

            - Two way radios, flashlights, smoke generation devices and supplies.

            - Spare printer paper.

            - A manufacturer recommended device for measuring air flow through air duct smoke detector sampling assemblies.

            - Decibel meter.

          - In addition to the testing specified to be performed by the installing Contractor, the installation shall be subject to test by the acceptance inspector.

          - System wiring: Fire alarm circuits shall be tested for continuity, grounds, and short circuits.

        - Acceptance testing

          - A written acceptance test procedure (ATP) for testing the fire alarm system components and installation will be prepared by the engineer in accordance with NFPA 72, NFPA 72E NFPA 72H and this specification. The Contractor shall be responsible for the performance of the ATP, demonstrating the function of the system and verifying the correct operation of all system components, circuits, and programming.

          - A program matrix shall be prepared by the installing Contractor referencing each alarm input to every output function affected as a result of an alarm condition on that input. In the case of outputs programmed using more complex logic functions involving "any", "or", "not", "count", "time", and "timer" statements; the complete output equation shall be referenced in the matrix.

          - A complete listing of all device labels for alphanumeric annunciator displays and logging printers shall be prepared by the installing contractor prior to the ATP.

          - The acceptance inspector shall use the system record drawings in co-ordination with the documents specified under paragraph 3.01 during the testing procedure to verify operation as programmed.

          - In conducting the ATP, the acceptance inspector shall request demonstration of any or all input and output functions. The items tested shall include but not be limited to the following:

            - System wiring shall be tested to demonstrate correct system response and correct subsequent system operation in the event of:

              - Open, shorted and grounded intelligent analog signaling circuit.

              - Open, shorted and grounded network signaling circuit.

              - Open, shorted and grounded conventional zone circuits.

              - Open, shorted and grounded speaker, telephone circuits.

              - Intelligent device removal.

              - Primary power or battery disconnected.

              - Incorrect device at address.

              - Printer trouble, off line or out of paper.

            - System evacuation alarm indicating appliances shall be demonstrated as follows:

              - All alarm notification appliances actuate as programmed.

              - Audibility and visibility at required levels.

            - System indications shall be demonstrated as follows:

              - Correct message display for each alarm input at the control panel, each remote alpha-numeric display and each LCD terminal.

              - Correct annunciator light for each alarm input at each annunciator and color graphic terminal as shown on the Drawings.

              - Correct printer logging for all system activity.

            - System off-site reporting functions shall be demonstrated as follows:

              - Correct zone transmitted for each alarm input.

              - Trouble signals received for disconnect.

            - Secondary power capabilities shall be demonstrated as follows:

              - System primary power shall be disconnected for a period of time as specified herein. At the end of that period, an alarm condition shall be created and the system shall perform as specified for a period as specified.

              - System primary power shall be restored for 48 hours and system charging current shall be normal trickle charge for a fully charged battery bank.

              - System battery voltages and charging currents shall be checked at the fire alarm control panel using the test codes and displayed on the LCD display.

            - Fireman's HVAC override system functions shall be demonstrated as follows:

              - Operation of key lockout switch preventing unauthorized operation of controls.

              - On/off control of each controlled element and test for interaction of other automatic and manual control functions while in the over-ride mode.

              - Correct status display of monitored elements.

              - Correct logging of activity to printer and historical memory as programmed.

          - In the event of system failure to perform as specified and programmed during the ATP procedure, at the discretion of the acceptance inspector, the test shall be terminated.

            - The installing Contractor shall retest the system, correcting all deficiencies and providing test documentation to the acceptance inspector.

            - The acceptance inspector may elect to require the complete ATP to be performed again if, in his opinion, modifications to the system hardware or software warrant complete retesting.

            - Changes made to a systems configuration program required by the acceptance inspector or to comply with the systems operating parameters shall be validated to insure that in making the software programming change no other part of the systems operation was effected. The validation shall utilize system software which meets the requirements of NFPA 72 section 7-1.6 "System Reacceptance Testing" as specified in the NFPA 72 National Fire Alarm Code 1993 edition. Change validation methods other than that described will not be considered acceptable and shall allow the acceptance inspector to require the complete ATP to be performed again.

      - DOCUMENTATION

        - System documentation shall be furnished to the owner and shall include but not be limited to the following:

          - System record drawings and wiring details including one set of reproducible masters and drawings electronic format.

          - System operation, installation and maintenance manuals.

          - Written documentation for all logic modules as programmed for system operation with a matrix showing interaction of all input signals with output commands.

          - Documentation of system voltage, current and resistance readings taken during the installation, testing and ATP phases of the system installation.

          - System program showing system functions, controls and labeling of equipment and devices.

      - TEST EQUIPMENT

        - Furnish all test equipment as required to program devices and test the system, specifically an intelligent device tester and programmer.

      - SERVICES

        - Warrant the entire system against mechanical and electrical defects for a period described in the Contract general conditions. This period shall begin upon completed certification and test of the system or upon first beneficial use of the system, whichever is earlier.

        - The fire alarm system Subcontractor or manufacturer shall offer for the Owners consideration at the time of system submittal a priced inspection, maintenance, testing and repair contract in full compliance with the requirements of NFPA 72 H.

          - The services offered under this Contract shall be performed during the first year after system acceptance and the Owner shall have the option of renewing for single or multiple years up to five years at the price quoted upon completion of the warranty period.

          - The Contractor performing the contract services shall be qualified and listed to maintain ongoing certification of the completed system to the UL for specific installed system listing.

        - The installation Contractor shall furnish training as follows for a minimum of four employees of the system user:

          - Training in the receipt, handling and acknowledgement of alarms.

          - Training in the system operation including manual control of output functions from the system control panel.

          - Training in the testing of the system including logging of detector sensitivity, field test of devices and response to common troubles.

          - The total training requirement shall be a minimum of 24 hours, conducted on three successive days, but shall be sufficient to cover all items specified.

END OF SECTION