- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Cable trays.

      - REFERENCES

        - BS EN ISO 1416

        - BS 729.

        - Local Codes and Standards.

        - Telecom Service provider regulations and requirements.

      - SUBMITTALS

        - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

        - Shop Drawings: Indicate tray type, dimensions, support points, and finishes.

        - Method statement for system’s component installation, testing and commissioning.

        - Product Data: Submit fittings and accessories.

        - Manufacturer's Installation Instructions: Submit application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements. Include instructions for storage, handling, protection, examination, preparation, and installation of Product.

        - Provide samples of all proposed cable trays, fittings, accessories...etc, together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

      - CLOSEOUT SUBMITTALS

        - Comply with requirements of Division 01.

        - Project Record Documents: Record actual routing of cable tray and locations of supports.

      - QUALIFICATIONS

        - Manufacturer: Company specializing in manufacturing Products specified in this section with minimum Five years documented experience.

        - The firm installing cable trays for communication systems shall have had a minimum of 5 years documented prior successful installation experience with systems similar in scope to the system of this project.

      - QUALITY ASSURANCE

        - Cable Trays shall comply with the applicable standards of Local Standards Organization and BS.

        - Any defects or damage caused partly or wholly in the installation of cable trays to the building or building fabric shall be made good to the satisfaction of the Engineer.

        - Source Limitations: Obtain cable tray components through one source from a single Manufacturer.

      - DELIVERY, STORAGE AND HANDLING

        - All Cable Trays shall be delivered in factory pack wrapping and boxes and stored in a clean, dry space within the racks.

      - SPARE PARTS

        - Supply as maintenance stock, additional consumable material of all types and sizes used, per Supplier’s recommendations.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the Engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - CABLE TRAYS

        - All cable trays shall be of heavy duty perforated type with return flange.

        - All cable trays shall be manufactured from hot-dip zinc coated galvanized steel, with a standard heavy duty galvanizing coating of 350 g/m2 and Z2 bending grade.

        - All accessories and fittings such as bends, tees, elbows, cross units and angles shall be of the same specification as that of the cable tray finish and shall be standard products from the same manufacturer as the cable tray. Site fabrication shall not be permitted.

        - Cable trays and accessories shall be of a thickness of not less than:

          - 1.5 mm up to 305 mm width.

          - 2 mm above 305 mm width.

        - All fixing brackets, nuts and bolts shall be finished by hot dip galvanizing.

        - Tinned copper earth continuity straps shall be provided at every joint of the cable tray.

        - Where cable tray crosses building expansion joints, the tray shall be installed suitably to provide expansion / contraction with the building expansion.

        - In outdoor locations and areas subject to corrosive atmospheres, all cable trays shall be painted with chlorinated rubber paint or PVC/Epoxy coating, as approved by the Engineer.

      - WARNING SIGNS

        - Engraved Nameplates: black letters on yellow laminated plastic nameplate, engraved with: WARNING! DO NOT USE CABLE TRAY AS WALKWAY, OR SUPPORT. USE ONLY AS MECHANICAL SUPPORT FOR CABLES AND TUBING!

- EXECUTION

      - INSTALLATION

        - Install cable tray level and plumb according to manufacturer's written instructions, Coordination Drawings, original design, and referenced standards.

        - Each run is to be completed before installation of cables.

        - Remove burrs and sharp edges from cable trays. Fix trays using approved suspension rods or steel angle brackets at spacing not exceeding 1.5 m and generally as shown on the Drawings.

        - Cables: Secure to tray with purpose made straps or saddles and arrange in one layer only, evenly spaced, or as shown on the Drawings, with minimum spacing of one diameter of the larger of the two adjacent cables or of a trefoil formation of single core cable circuit.

        - Fasten cable tray supports securely to building structure as specified in Division 16 Section "Basic Electrical Materials and Methods," unless otherwise indicated.

        - Subparagraph below is a conservative design requirement for usual applications.

        - Design supports, including fastenings to the structure, to carry the greater of the calculated load multiplied by a safety factor of 4. Submit calculations for approval.

        - Delete paragraph below if cable tray / ladder does not connect to equipment.

        - Make connections to equipment with flanged fittings fastened to cable tray and to equipment.  Support cable tray independently of fittings.  Do not carry weight of cable tray on equipment enclosure.

        - Delete paragraph below if expansion fittings are not required.

        - Install expansion connectors where cable tray crosses a building expansion joint and in cable tray runs that exceed 27 m. Make changes in direction and elevation using standard fittings.

        - Make cable tray connections using standard fittings.

        - Locate cable tray above piping, unless accessibility to cable tray is required or unless otherwise indicated.

        - Seal penetrations through fire and smoke barriers according to Division 7 Section "Through-Penetration Firestop Systems."

        - If cable trays / ladders are sized for future cables, specify provisions for penetrations with sleeves through fire-rated partitions, or use "repairable" fire stopping-penetration sealing material.

        - Sleeves for Future Cables: Install capped sleeves for future cables through fire stopping-sealed cable tray penetrations of fire and smoke barriers.

        - Workspace:  Install cable trays with sufficient space to permit access for installing cables. Minimum clearance of 250 mm is to be maintained between top of tray and ceiling, beams and other services and between tray in multi-tier formation.

        - Delete paragraph below if systems are not mixed.

        - Barriers: Where tray carries conductors of different systems, such as power, communications and data processing, or different insulation levels, such as 600V, 5000V, and 20, 000 V use separate cable tray.  In case of absolute necessity, install insulating barriers to separate the systems after obtaining the Engineer’s approval.

        - Install covers after installation of cable is completed.

        - Install warning signs at centers along cable tray, located to be visible.

- END OF SECTION