- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - This section specifies general grounding and bonding requirements of electrical systems and installations (Low voltage), grounding and bonding of all electrically operated equipment’s, grounding and bonding of all metal raceways (metal conduits, cable trays, trucking, cable ladders), bonding and grounding of all piping/ ducting networks and metal structures/ installations.

      - REFERENCES

        - BS 7430: 1998 - Code of practice for earthing

        - BS EN 13601:2002 - Copper and copper alloys. Copper rod, bar and wire for general electrical purposes

        - British Standard Code of Practice CP1013 - Grounding.

        - BS 7671 IEE Wiring Regulations, 17th Edition with all current additions and amendments.

        - Requirements of Local Authorities and electrical/ telecom service providers.

        - Local Codes and Regulations

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

        - Provide samples of all proposed grounding and bonding system parts, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Method statement for installation, testing and commissioning of the Grounding and Bonding systems.

        - Full calculation test report for the system from the system supplier.

        - Detailed dimensional workshop drawings for all earthing and Grounding systems with all sections, details and routings.

        - Detailed dimensional workshop drawings for earthing systems of transformers, generators, main low voltage distribution system, and main low current system signed and stamped from the related power utility/ service providers.

        - Soil resistivity tests reports.

        - Manufacturer's Installation Instructions: Submit for active electrodes.

        - Manufacturer's Certificate: Certify Products meet or exceed specified requirements.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations of components and grounding electrodes.

      - QUALITY ASSURANCE

        - Manufacturer’s: Firms regularly engaged in the manufacture of Grounding equipment, whose products have been in satisfactory use in similar service for not less than 10 years.

        - All equipment furnished under these Specifications shall conform to the requirements of BS, IEC and Local Standards Organization.

        - Maintain one copy of each document on site.

      - QUALIFICATIONS

        - Manufacturer: Company specializing in manufacturing Products specified in this section with minimum three years documented experience.

        - Installer: Company specializing in performing work of this section with minimum three years documented experience approved by manufacturer.

      - DELIVERY, STORAGE AND HANDLING

        - Product Requirements: Requirements for transporting, handling, storing, and protecting

        - Accept materials on site in original factory packaging, labeled with manufacturer's identification.

        - Protect from weather and construction traffic, dirt, water, chemical, and mechanical damage, by storing in original packaging.

      - COORDINATION

        - Complete grounding of equipment and bonding to building grounding system through bonding to building’s reinforcing steel prior concrete placement.

        - Prior to any material ordering, installation the Contractor shall coordinate with Local power utility/ service provider and get their approval on the system drawings by getting all systems drawings signed and stamped by them.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out periodic testing and maintenance for the system, without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - All the materials required for Grounding system shall be furnished new and undamaged in accordance with the requirement stated in this section.

        - Conduct soil electrical resistively tests at four locations (minimum) advised by the Engineer. The Grounding calculations based on the test results shall be submitted for Engineers approval, to demonstrate that the proposed design of Grounding system complies with the specifications and standards.

        - For communication room, separate Grounding pits shall be installed as per Local Telephone Supplier requirements, which will be isolated from the main Grounding loop.

        - Underground direct buried 25X3 mm stranded bare copper cable install at 1000mm FFL use around the building for grounding and bonding as shown on drawing

      - GROUNDING RODS

        - Grounding rods shall conform to BS requirements.

        - Grounding rods of the (copper clad rods constructed with a minimum of 0.25 mm thick copper exterior sleeve inseparably and permanently clamp to a central high tensile steel core for rigidity) type shall be used.

        - Grounding rods shall be copper-clad steel 16 mm diameter with min. 1200mm length. For extra lengths, rods shall be coupled together using threaded copper alloy couplings.

        - The terminal end of grounding rod shall finish 300mm below finished ground level covered by a concrete inspection pit of size 300mmX300mm with concrete cover.

        - Grounding electrodes for each system shall have an interconnected resistance to Grounding of not more than 1 Ohms. Where this value is exceeded it shall be augmented by additional electrodes connected in parallel spaced at approximately four meters apart until this value is reached.

      - GROUNDING CONDUCTORS

        - Size of Grounding conductors shall be as shown on the drawings and in accordance with the applicable standards.

        - Grounding conductors shall be as follows:

- 1.   	Outdoor underground: Soft drawn bare high conductivity annealed plain stranded copper   conductor.

- 2.	       Inside building: Same as for outdoor conductor but with green/yellow colored polyvinyl chloride (PVC) insulation.

        - PVC insulated copper conductor cable shall be used for final connections from grounding loop to structures, equipment, etc. and for Grounding/bonding of equipment and metalwork inside the building.

        - All copper to copper connections, splices, taps, etc. in conductor and at the accessories for termination shall be made by the exothermic clamp. Joints for underground installation shall be epoxy resin encapsulated before burial.

        - The Grounding conductor in the conduit shall be continuous through the conduit run with bushing Grounding connection and terminated on the panel board Grounding.

      - GROUNDING CONNECTION BAR

        - For connection of MV and LV equipment, sub-station shall have high conductivity copper, Grounding connection bar with minimum dimensions of 50 x 6 mm and mounted on porcelain insulators. The bar shall be of suitable length with pre-drilled holes at a minimum distance of 50 mm between whole centers.

        - Grounding connection bars for LV switchboard frame shall be separate from Grounding bar for MV and transformer frame.

        - Grounding connection bar shall have a permanent label to identify the connections together with the wording "Main Grounding Bar".

- EXECUTION

      - INSPECTION

        - Examine the area and conditions under which the Grounding systems are to be installed and correct any unsatisfactory conditions detrimental to the timely and proper completion of the work. Do not proceed with the work until the conditions are satisfactory in a manner acceptable to the Engineer.

      - GENERAL INSTALLATION REQUIREMENTS

        - The installation shall be carried out in accordance with IEE Wiring Regulations, 17th Edition. The position of all conductors, joints and terminals shall be approved by the Engineer prior to commencing the work.

        - All electrical equipment shall be connected to the Grounding with copper Grounding conductor. The term "electrical equipment" shall include all metal enclosures containing electrical connections or bare conductors. Individual devices such as solenoids, pressure switches, and limit switches shall be exempt from this requirement unless the device requires Grounding for proper operation. Large equipment such as power distribution board or motor control centers shall be furnished with a Grounding bus, which shall be connected at two points to the Grounding. All Grounding connection surfaces shall be cleaned immediately prior to connection. Provide all Grounding material required but not furnished with the equipment.

        - All exposed non-current carrying metallic parts of all the installations shall be effectively grounded. The steel conduit systems, metallic equipment enclosures, metallic lighting fixtures, cable trays, all non-current carrying metal parts of electrical systems and any other equipment or system components shall be grounded and the connection shall be extended to the nearest panel board Grounding or grounding bar in sub-station.

        - The conductive sheaths and armor of cables shall be connected to grounding.

        - All connections and joints for the grounding system including bonding connections shall be made using "Exothermic" process which produces a fused joint.

      - 3.03	GROUNDING RODS INSTALLATION

        - All grounding rods shall be installed at suitable locations and to the depth to achieve required resistance. Where the grounding rod length exceeds 2.5 m, standard sections shall be connected with aluminum bronze coupling to extend the rod.

        - Grounding rods shall be driven with a cap driving stud.

        - All connections between rods and grounding conductors shall be made by removable bolted connection.

        - All grounding rods shall have inspection pits as shown on Drawings. The pit shall be constructed from pre-cast concrete. All connections to the grounding rod shall be exposed when the cover is raised. Attach a “DANGER - ELECTRICITY” sign to the wall of the inspection pit. Use English and Arabic white letters on red background. Inspection pit cover shall be constructed from cast iron.

      - GROUNDING CONDUCTORS INSTALLATION

        - Standard sizes of stranded copper conductor used for Grounding continuity shall be according to the requirements of IEE Wiring Regulations, 17th Edition.

        - Suitable Grounding facilities, acceptable to the Engineer, shall be furnished on electrical equipment to consist of compression type terminal connectors bolted to the equipment frame or enclosure and providing a minimum of joint resistance.

        - The conduit system shall not be considered as continuous for Grounding purposes. A separate Grounding conductor shall be installed in the same conduit with the phase and neutral conductors. The separate Grounding conductors shall be sized according to IEE Wiring Regulations, 17th Edition Requirements. No Grounding conductors shall be smaller than 2.5 mm2 unless this is part of a multicore cable. Where flexible connections are made to equipment, grounding jumpers shall be provided. All connections of heavy gauge steel conduit system shall be checked for good electrical continuity.

        - Exposed conductors shall be installed inconspicuously in vertical or horizontal positions on supporting structures. When located on irregular supporting surfaces or equipment, the conductors shall run parallel to or normal to the dominant surface.

        - Conductors routed over concrete, steel or equipment surfaces shall be kept in close contact with those surfaces by using fasteners located at intervals not exceeding 1 m.

        - Exposed Grounding conductors shall be securely fastened to the mounting surface using copper or brass straps.

        - Clamps, connectors, bolts, washers, nuts and other hardware for bolted connection to Grounding system shall be of copper.

        - The Grounding conductors entering the building shall be installed in a 25 mm diameter PVC conduit. Waterproofing shall be provided at all entry of Grounding conductors, details of which shall be approved by the structural engineer.

        - Grounding conductors shall be buried at a minimum depth of 800 mm below finished grade.

        - Underground conductors shall be buried in clean sifted Grounding.

        - Except for sub-stations and electric rooms, the exposed Grounding conductor shall run in protective pipes for runs below 900 mm from floor level. Pipe shall also be provided at locations where conduct is likely to be subject to physical damage.

        - Extensions from Grounding loop as shown on the Drawings shall be provided for connection to electrical equipment. Connect the Grounding conductor to the equipment, Grounding bus, pad or lug. In addition to the Grounding grid extension conductors, a Grounding cable to each end of the Grounding bus in each assembly of power distribution board or panel boards shall be provided.

        - Where a Grounding conductor is included with the phase conductors of power circuits, the Grounding conductor shall be connected to the equipment Grounding facilities and to the source Grounding bus. Where a grounding conductor is not included with the phase conductors, the equipment shall be grounded by connecting a separate Grounding cable to the equipment Grounding facilities and to the tray Grounding cable or source Grounding bus. Except where otherwise shown on the Drawings, integral parts of a cable assembly shall be sized in accordance with the requirements of IEE Wiring Regulations, 17th Edition.

      - GROUNDING LOOP IMPEDANCE

        - The completed Grounding system shall have sufficiently low impedance to limit the voltage to grounding and to facilitate the operation of the current protective devices in the circuit. Grounding loop impedance shall not exceed the values specified in BS or other applicable standards.

      - BUILDING SYSTEMS GROUNDING

        - The building low current systems including communication, control and alarm functions…etc. shall be provided with Grounding as shown on the Drawings and in relevant specifications.

        - The installation of the Grounding for building systems shall be in accordance with the recommendations of standards, and the applicable provisions of this section.

      - FIELD QUALITY CONTROL

        - Grounding resistance tests shall be carried out after installation of the individual Grounding systems in accordance with the Specifications. The Grounding resistance tests shall be carried out in accordance with Section 713-11 of the IEE Wiring Regulations 17th Edition and readings obtained officially recorded by all witnessing parties.

        - Prior to connection of Grounding rods to the Grounding system, the Grounding resistance of individual Grounding rod shall be measured by using an approved type of Grounding resistance tester.

        - After completion of all the connections of Grounding system, the Grounding resistance shall be measured from the Grounding test point in presence of the Engineer.

        - All the Grounding resistance test reports shall be submitted for Engineer’s approval.

- END OF SECTION