SECTION 23 0713
DUCT INSULATION

PART 1 GENERAL

- SECTION INCLUDES

- Duct insulation.

- Duct Liner.

- Insulation jackets.

- RELATED REQUIREMENTS

- Section 07 8400 - Firestopping.

- Section 09 9113 - Exterior Painting: Painting insulation jackets.

- Section 09 9123 - Interior Painting: Painting insulation jackets.

- Section 22 0553 - Mechanical Identification.

- Section 23 0553 - Identification for HVAC Piping and Equipment.

- Section 23 3100 - HVAC Ducts and Casings: Glass fiber ducts.

- REFERENCE STANDARDS

- ASTM B209 - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate; 2014.

- ASTM B209M - Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate [Metric]; 2014.

- ASTM C518 - Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus; 2010.

- ASTM C553 - Standard Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications; 2013.

- ASTM C612 - Standard Specification for Mineral Fiber Block and Board Thermal Insulation; 2014.

- ASTM C916 - Standard Specification for Adhesives for Duct Thermal Insulation; 2014.

- ASTM C1071 - Standard Specification for Fibrous Glass Duct Lining Insulation (Thermal and Sound Absorbing Material); 2012.

- ASTM C1290 - Standard Specification for Flexible Fibrous Glass Blanket Insulation Used to Externally Insulate HVAC Ducts; 2011.

- ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials; 2015a.

- ASTM E96/E96M - Standard Test Methods for Water Vapor Transmission of Materials; 2014.

- ASTM G21 - Standard Practice for Determining Resistance of Synthetic Polymeric Materials to Fungi; 2015.

- SMACNA (DCS) - HVAC Duct Construction Standards Metal and Flexible; 2005 (Rev. 2009).

- UL 723 - Standard for Test for Surface Burning Characteristics of Building Materials; Underwriters Laboratories Inc.; Current Edition, Including All Revisions.

- SUBMITTALS

- Product Data: Provide product description, thermal characteristics, list of materials and thickness for each service, and locations.

- Samples: Submit two samples of any representative size illustrating each insulation type.

- Manufacturer's Instructions: Indicate installation procedures necessary to ensure acceptable workmanship and that installation standards will be achieved.

- QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in manufacturing products of the type specified in this section with not less than ten years of documented experience.

- Applicator Qualifications: Company specializing in performing the type of work specified in this section, with minimum five years of experience.

- DELIVERY, STORAGE, AND HANDLING

- Accept materials on site in original factory packaging, labelled with manufacturer's identification, including product density and thickness.

- Protect insulation from weather and construction traffic, dirt, water, chemical, and mechanical damage, by storing in original wrapping.

- FIELD CONDITIONS

- Maintain ambient temperatures and conditions required by manufacturers of adhesives, mastics, and insulation cements.

- Maintain temperature during and after installation for minimum period of 24 hours.

PART 2 PRODUCTS

- REGULATORY REQUIREMENTS

A. Surface Burning Characteristics: Flame spread index/Smoke developed index of 25/50, maximum, when tested in accordance with ASTM E84 or UL 723.

- OUTDOOR INSTALLATION

A. Thermal insulation of outdoor rectangular ductwork shall be foil faced rigid MINERAL

WOOL/MINERAL FIBRE, Anti microbial (Anti Fungal), noncombustible slab consisting of long fine fibres (free from short and coarse fibres) in accordance with BS EN 13162 and bonded with a temperature resistant resin and CE marked. The thickness shall be at least 50mm, density shall be a minimum of 48 kg/m3 and thermal conductivity shall be less than 0.038 W/m.K at 24°C.

- IN SHAFT ISTALLATION

A. Thermal insulation of indoor rectangular ductwork shall be foil faced flexible rock wool/mineral fibre, Anti microbial (Anti Fungal), noncombustible material consisting of long fine fibres (free from shot and coarse fibres) made up in mat form in accordance with BS EN 13162 and CE marked. The thickness shall be at least 50 mm, density shall be a minimum of 48 kg/m3 and thermal conductivity shall be less than 0.038 W/m.K at 24°C.

- INDOOR INSTALLATION

A. Thermal insulation of indoor rectangular ductwork shall be foil faced flexible rock wool/mineral fibre, Anti microbial (Anti Fungal), noncombustible material consisting of long fine fibres (free from shot and coarse fibres) made up in mat form in accordance with BS EN 13162 and CE marked. The thickness shall be at least 25 mm, density shall be a minimum of 32 kg/m3 and thermal conductivity shall be less than 0.038 W/m.K at 24°C.

- ACOUSTIC USE

A. Where there is a requirement to prevent noise transmission through the walls of the ductwork, either in the form of noise breakout prior to an attenuator, noise break-in on the attenuated side, acoustic insulation shall be applied to the external surface of the ductwork. The acoustic insulation shall be of an approved noise control barrier of rock wool/mineral fibre, Anti microbial (Anti Fungal), noncombustible, with a minimum density of 64 Kg/m3. The acoustic insulation shall be at least 50mm thick and the thermal conductivity less than or equal to 0.04 W/mK.

- JACKETS

- Canvas Jacket: UL listed 220 g/sq m (6 oz/sq yd) plain weave cotton fabric treated with dilute fire retardant lagging adhesive.

- Lagging Adhesive:

a. Compatible with insulation.

- Aluminum Jacket: ASTM B209 (ASTM B209M).

- Thickness: 0.64 mm thick sheet.

- Finish: Embossed.

- Joining: Longitudinal slip joints and 50 mm laps.

- Fittings: 0.4mm thick die shaped fitting covers with factory attached protective liner.

- Metal Jacket Bands: 0.38 mm thick aluminum.

All duct that are thermally insulated and exposed to outdoor weather or located inside technical area shall be provided with Aluminium Jacket

- DUCT LINER

A. Where there is a requirement to internally line the ductwork or plenum to attenuate airborne noise the acoustic lining material shall be of an approved noise control barrier of closed cell elastomeric type to prevent fragmentation with a minimum thickness of 25mm and a thermal conductivity less than or equal to 0.037. Liner must be fastened in a secure manner to the Engineer's approval.

PART 3 EXECUTION

- EXAMINATION

- Verify that ducts have been tested before applying insulation materials.

- Verify that surfaces are clean, foreign material removed, and dry.

- INSTALLATION

- Install in accordance with manufacturer's instructions.

- Install in accordance with NAIMA National Insulation Standards.

- Insulated ducts conveying air below ambient temperature:

- Provide insulation with vapor barrier jackets.

- Finish with tape and vapor barrier jacket.

- Continue insulation through walls, sleeves, hangers, and other duct penetrations.

- Insulate entire system including fittings, joints, flanges, fire dampers, flexible connections, and expansion joints.

- Insulated ducts conveying air above ambient temperature:

- Provide with or without standard vapor barrier jacket.

- Insulate fittings and joints. Where service access is required, bevel and seal ends of insulation.

- Ducts Exposed in Mechanical Equipment Rooms or Finished Spaces where exposed to mechanical loads: Finish with canvas jacket sized for finish painting. Do not jacket duct running above ceiling if not exposed to mechanical load, impact or prone to damage.

- Exterior (outdoor) Applications: Provide insulation with vapor barrier jacket. Cover with with calked aluminum jacket with seams located on bottom side of horizontal duct section.

- External Duct Insulation Application:

- Secure insulation with vapor barrier with wires and seal jacket joints with vapor barrier adhesive or tape to match jacket.

- Install without sag on underside of duct. Use adhesive or mechanical fasteners where necessary to prevent sagging. Lift duct off trapeze hangers and insert spacers.

- Seal vapor barrier penetrations by mechanical fasteners with vapor barrier adhesive.

- Stop and point insulation around access doors and damper operators to allow operation without disturbing wrapping.

- Duct and Plenum Liner Application:

- Adhere insulation with adhesive for 90 percent coverage.

- Secure insulation with mechanical liner fasteners. Refer to SMACNA (DCS) for spacing.

- Seal and smooth joints. Seal and coat transverse joints.

- Seal liner surface penetrations with adhesive.

- Duct dimensions indicated are net inside dimensions required for air flow. Increase duct size to allow for insulation thickness.

END OF SECTION