SECTION 23 3300
AIR DUCT ACCESSORIES

PART 1 GENERAL

- SECTION INCLUDES

- Air turning devices/extractors.

- Backdraft dampers - metal.

- Combination fire and smoke dampers.

- Duct access doors.

- Duct test holes.

- Flexible duct connections.

- Volume control dampers.

- RELATED REQUIREMENTS

- Section 07 8400 - Firestopping.

- Section 23 0548 - Vibration and Seismic Controls for HVAC Piping and Equipment.

- Section 23 3100 - HVAC Ducts and Casings.

- Section 23 3600 - Air Terminal Units: Pressure regulating damper assemblies.

- Section 26 2717 - Equipment Wiring: Electrical characteristics and wiring connections.

- REFERENCE STANDARDS

- NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilating Systems; National Fire Protection Association; 2015.

- NFPA 92 - Standard for Smoke-Control Systems; 2015.

- NFPA 96 - Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations; 2014.

- SMACNA (DCS) - HVAC Duct Construction Standards Metal and Flexible; Sheet Metal and Air Conditioning Contractors' National Association; 2005.

- UL 33 - Standard for Safety Heat Responsive Links for Fire-Protection Service; Underwriters Laboratories Inc.; Current Edition, Including All Revisions.

- UL 555 - Standard for Fire Dampers; Underwriters Laboratories Inc.; Current Edition, Including All Revisions.

- UL 555S - Standard for Smoke Dampers; Underwriters Laboratories Inc.; Current Edition, Including All Revisions.

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements, for submittal procedures.

- Product Data: Provide for shop fabricated assemblies including volume control dampers. Include electrical characteristics and connection requirements.

- Shop Drawings: Indicate for shop fabricated assemblies including volume control dampers.

- Manufacturer's Installation Instructions: Provide instructions for fire dampers.

- Project Record Drawings: Record actual locations of access doors and test holes.

- Maintenance Materials: Furnish the following for Employer/Owner's use in maintenance of project.

- See Section 01 6000 - Product Requirements, for additional provisions.

- Extra Fusible Links: One of each type and size.

- QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

- Products Requiring Electrical Connection: Listed and classified by Underwriters Laboratories Inc. as suitable for the purpose specified and indicated.

- DELIVERY, STORAGE, AND HANDLING

- Protect dampers from damage to operating linkages and blades.

PART 2 PRODUCTS

- AIR TURNING DEVICES/EXTRACTORS

- Multi-blade device with radius blades attached to pivoting frame and bracket, galvanized steel construction, with push-pull operator strap.

- BACKDRAFT DAMPERS - METAL

- Multi-Blade, Parallel Action Gravity Balanced Backdraft Dampers: Galvanized steel, with center pivoted blades of maximum 150 mm (6 inch) width, with felt or flexible vinyl sealed edges, linked together in rattle-free manner with 90 degree stop, steel ball bearings, and plated steel pivot pin; adjustment device to permit setting for varying differential static pressure.

- DUCT ACCESS DOORS

A. Fabricate in accordance with SMACNA (DCS) and as indicated.

- DUCT TEST HOLES

- Temporary Test Holes: Cut or drill in ducts as required. Cap with neat patches, neoprene plugs, threaded plugs, or threaded or twist-on metal caps.

- Permanent Test Holes: Factory fabricated, air tight flanged fittings with screw cap. Provide extended neck fittings to clear insulation.

- FLEXIBLE DUCT CONNECTIONS

- Fabricate in accordance with SMACNA (DCS) and as indicated.

- Flexible Duct Connections: Fabric crimped into metal edging strip.

- Fabric: UL listed fire-retardant neoprene coated woven glass fiber fabric to NFPA 90A, minimum density 1.0 kg/sq m (30 oz per sq yd).

a. Net Fabric Width: Approximately 50 mm (2 inches) wide.

- Metal: 75 mm (3 inches) wide, 0.61 mm (24 gage, 0.0239 inch) thick galvanized steel.

- Leaded Vinyl Sheet: Minimum 14 mm (0.55 inch) thick, 4.2 kg/sq m (0.87 lbs per sq ft), 10 dB attenuation in 10 to 10,000 Hz range.

- Maximum Installed Length: 356 mm (14 inch).

- VOLUME CONTROL DAMPERS

- Fabricate in accordance with SMACNA (DCS) and as indicated.

- Splitter Dampers:

- Material: Same gage as duct to 600 mm (24 inches) size in either direction, and two gages heavier for sizes over 600 mm (24 inches).

- Blade: Fabricate of single thickness sheet metal to streamline shape, secured with continuous hinge or rod.

- Operator: Minimum 6 mm (1/4 inch) diameter rod in self aligning, universal joint action, flanged bushing with set screw .

- Single Blade Dampers: Fabricate for duct sizes up to 150 x 760 mm (6 x 30 inch).

- Fabricate for duct sizes up to 150 by 450 mm (6 by 18 inch).

- Blade: 0.61 mm (24 gage, 0.0239 inch), minimum.

- Multi-Blade Damper: Fabricate of opposed blade pattern with maximum blade sizes 200 x 1825 mm (8 x 72 inch). Assemble center and edge crimped blades in prime coated or galvanized channel frame with suitable hardware.

1. Blade: 1.21 mm (18 gage, 0.0478 inch), minimum.

- End Bearings: Except in round ducts 300 mm (12 inches) and smaller, provide end bearings. On multiple blade dampers, provide oil-impregnated nylon, thermoplastic elastomer, or sintered bronze bearings.

PART 3 EXECUTION

- PREPARATION

A. Verify that electric power is available and of the correct characteristics.

- INSTALLATION

A. Install accessories in accordance with manufacturer's instructions, NFPA 90A, and follow SMACNA (DCS). Refer to Section 23 3100 for duct construction and pressure class.

- Provide backdraft dampers on exhaust fans or exhaust ducts nearest to outside and where indicated.

- Provide duct access doors for inspection and cleaning before and after filters, coils, fans, automatic dampers, at fire dampers, combination fire and smoke dampers, and elsewhere as indicated. Provide for cleaning kitchen exhaust ducts in accordance with NFPA 96. Provide minimum 200 by 200 mm (8 by 8 inch) size for hand access, size for shoulder access, and as indicated. Provide 100 by 100 mm (4 by 4 inch) for balancing dampers only. Review locations prior to fabrication.

- Provide duct test holes where indicated and required for testing and balancing purposes.

- Provide fire dampers, combination fire and smoke dampers, and smoke dampers at locations indicated, where ducts and outlets pass through fire rated components, and where required by Authorities Having Jurisdiction. Install with required perimeter mounting angles, sleeves, breakaway duct connections, corrosion resistant springs, bearings, bushings and hinges.

- Install smoke dampers and combination smoke and fire dampers in accordance with NFPA 92.

- Demonstrate re-setting of fire dampers to Employer/Owner's representative.

- At fans and motorized equipment associated with ducts, provide flexible duct connections immediately adjacent to the equipment.

- At equipment supported by vibration isolators, provide flexible duct connections immediately adjacent to the equipment.

1. Refer to Section 23 0548.

- For fans developing static pressures of 1250 Pa (5.0 inches) and over, cover flexible connections with leaded vinyl sheet, held in place with metal straps.

- Provide balancing dampers at points on supply, return, and exhaust systems where branches are taken from larger ducts as required for air balancing. Install minimum 2 duct widths from duct take-off.

- Use splitter dampers only where indicated.

- Provide balancing dampers on high velocity systems where indicated. Refer to Section 23 3600 - Air Terminal Units.

- Provide balancing dampers on duct take-off to diffusers, grilles, and registers, regardless of whether dampers are specified as part of the diffuser, grille, or register assembly.

END OF SECTION