- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Exterior and street lighting and area/façade lighting including, but not limited to, the following:

            - Exterior light fixtures.

            - Solar street  light fixtures.

            - Lighting Poles/Columns.

            - Lighting Controls.

      - REFERENCES

        - BS	British Standards

        - IEC        International Electro - technical Commission.

        - Local Codes and regulations.

        - All steel items , bolt , nuts and washers hot dip galvanized (EN ISO 1461)

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years’ period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

        - Provide samples all poles, light fittings, lamps, control gears, LED drives, boxes, fittings, etc. and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Provide method statement for installation, testing and commissioning of external lighting poles, landscape/ façade.

        - Dimensioned drawings of the light fixtures installations, including but not necessary limited to, the layout and connections to panel boards, fixture shop drawings in booklet form with separate sheet for each proposed fixture and accessories assembled in luminaire "type" alphabetical order.

      - QUALITY ASSURANCE

        - Manufacturer’s: Firms regularly engaged in manufacture of the lighting fixtures of types and ratings required, whose products have been in satisfactory used in similar service for not less than 10 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation and experience on projects with the lighting fixtures similar to that required for the project.

        - The exterior and street lighting fixtures shall comply with applicable requirements of BS and IEC.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver the exterior light, landscape light, and street lighting fixtures, lamps and accessories to job site wrapped in protective covering and stored in a dry location free from dust or water, and in such a manner to permit easy access for inspection and handling. The light fixtures, lamps and accessories shall to be handled carefully to prevent damage. Replace damaged items at no additional cost.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 24 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - All materials specified herein shall be of high quality and of proven suitability for the functions they will perform and the conditions they will meet in service.

      - EXTERIOR   LIGHT FIXTURES

        - All exterior landscape light fixtures including area/ façade lights shall be complete with all necessary accessories such as ballasts lamps, sockets, reflectors, mounting hardware, etc., to make a workable unit.

        - Exterior, landscape light fixtures shall be generally made of extruded or pressure die-cast and aluminum alloy housing with sheet aluminum corrosion resistance type and top sealed with fasteners and silicone sealant.

        - Optical system shall be composed of polished aluminum reflectors allowing field adjustment to the desired light distribution. Reflector shall be adjustable and retained in position by a spring loaded per device. Lens shall be clear flat tempered glass or acrylic. The external surface shall be smooth to reduce to minimum dirt and accumulation and, therefore maintenance.

        - All exterior, landscape light fixtures shall be dust and splash proof, conforming to the protection classification IP 54/65 or approved equivalent.

        - Any proposal for lighting fixtures other than specified fixtures shall be accompanied by complete lighting calculations and photometric for the proposed fixtures.

        - Comply with the requirements of Section 26 51 00, for exterior landscape light and street/ lighting fixtures, as applicable.

        - Ballasts and other components of the control gear of light fixtures shall be mounted on an inner tray with a cover and retained in the closed position by two quarter turn fasteners. The entire tray assembly shall be removable for replacement or maintenance. Some light fixtures may require remote mounting of the control gear; in this situation a detail showing construction of remote control gear and distance from the light fixture is shall be submitted for the approval of Engineer.

        - Ballasts to be of the ratings, types and makes as recommended by the manufacturers for starting the high intensity discharge lamp which properly matches lamps to power line by providing appropriate voltages and impedances for which lamps are designed.

      - SOLAR STREET   LIGHT FIXTURES

        - The scope of supply shall consist of the design, production of materials, manufacturing, drawings and data, assembly, painting, testing, inspection and all  in accordance with applicable codes and standards and any additional requirements of this specification, the Solar street light operates from Dusk to Dawn i.e., the lamp automatically switches ON after the sunset and switches OFF after sunrise.

        - The solar street lighting system basically consists of:

- Solar photovoltaic Module

- Luminaire/LED street light

- Low maintenance battery

- Pole and solar panel bracket

- Battery box

- Interconnecting cables.

        - The solar photovoltaic module is fixed firmly on top of the pole with suitable tilt and inclination so as to receive maximum sunlight throughout the day. The solar photovoltaic module thus produces suitable voltage and current, which is used to charge the battery inside the battery box. This energy stored in the battery is used to light up the LED which is housed inside the luminaire during night time.

        - Energy efficient LED street lamps of at suitable watts with 25 Lux requirements, an inverter and charge controller card, which is used to convert the stored DC energy in the battery to suitable AC voltage to ignite the LED. A reflector is provided in the LED street light to increase and spread the light uniformly. The charge controller protects the battery from over charge and deep discharge.

        - The Solar photovoltaic module, led street lamp and the battery box are fixed on to the Pole and are interconnected through the cables. The solar street light operates in the stand alone mode.

        - The solar battery is housed inside a battery box, which is underground or fixed on to the pole at a suitable height from the ground for easy maintenance and replacement. The battery provided shall be low maintenance tubular lead acid type. This requires minimal maintenance and has a long life with regular use. Periodical maintenance of the battery includes topping up distilled water once in 2-3 months and applying petroleum jelly to the terminals to prevent corrosion.

        - The Street lighting system shall be equipped with the following:

- -  12V/24V Solar Module Energy efficient LED street lamp of suitable Watts with min 25 Lux.

- - 1 or 2nos. of low/negligible maintenance batteries in an IP 65 enclosure.

- -  Pole with pedestal/mounting accessories

- - Automatic On/Off operation

- - Any other accessories not mentioned here but required for completion of the work and   proper Functioning of the solar street lighting system.

        - High efficiency, mono/multi crystalline silicon. Solar module designed to withstand tough environment conditions with test certificate.

        - Luminaire with transparent acrylic cover, housing a high efficiency LED street lamp fitted with gasket and accessories for weather and insect proof operation.

        - LED street lamp design shall be lighting area covered along the road is more compared to across the road i.e, at least 25 Lux/m at certain height of the pole.

        - One or Two battery, 12V or 24V spill proof, maintenance free batteries.

        - The solar street light pole must be made of MS and hot dip galvanized with powder coated. The pole shall be heavy duty and suitable for rural applications.

        - The led street lamp power achieve desired lux level.

        - 12 / 24 VDC nominal system voltages.

        - Minimum of 25 LUX at certain required height of pole choice

        - Inspection and Testing as per standards shall be performed on Solar System module for the prescribed lighting requirements.

        - Material used for Lighting columns, brackets and anchor bolts shall conform to applicable international standards and shall be hot dip galvanized.

        - A proper coding schedule, showing all relevant options for each type of solar lighting system so that any third party can “decode” an ordering code and determine the exact properties and options of the material.

        - The environmental conditions that shall be taken into account in the design, are as herein resumed:

Ambient temperature
              * minimum 0°C
              * maximum 55°C
              * surface exposed to sun 82 °C (Black Bulb Temp)

Rainfall
              * annual negligible mm
              * maximum hourly 25 mm
              Relative humidity
              * maximum 98%
              * minimum 30%
              * mean 74%
              Seismic conditions
              * ASCE-7/05 provisions not applicable

Climatic Area Classification

      - LAMPS

        - All lamps shall conform to Section 26 51 00.

      - LIGHTING POLES/COLUMNS

        - Lighting poles/columns for exterior landscape lighting and street lighting shall be manufactured of steel, with smooth exterior surface. The height, bottom and top diameters and other pertinent information regarding lighting poles/columns shall be as indicated on the Drawings, cut sheet and schedules.

        - Lighting poles/columns shall be supplied with steel plate base flange which shall include earthing nut, handhole with cover and four galvanized steel anchor bolts.

        - Lighting poles/columns shall be supplied with suitable brackets to accommodate the mounting of the type and number of light fixtures shown on the drawings, cut sheet and Schedules.

        - Anchor bolts shall be smooth or threaded bars and shall be used of a grade at least equivalent to the grade use for the shaft and a minimum of 75 mm long. No welding will be carried out on the bolts.

        - The lighting poles/columns shall be able to withstand a wind loading on the effective projected areas of pole, bracket and lighting fixtures. Foundations shall be in accordance with the structural requirements contained elsewhere in the specifications.

        - Treatment of metalwork:

- 1. All components shall be hot dipped galvanized by total immersion in a bath of molten zinc after completion of the fabrication. No further leveling up, finishing or modifications shall be carried out after galvanizing. Unless otherwise mentioned in drawings or bill of quantities, the minimum thickness of zinc coating shall be 450 gm/sq.m on the inside and outside faces of the mast and ring. The galvanizing shall conform with BS 729: 1971.

        - Lighting poles/columns used for exterior and street lighting shall be unpainted and have a frangible anchor base for pad mounting per AASHTO LTS 2. The poles shall be provided with a wiring compartment at a height suitable for access and maintenance. Provide fuse, with fuse holder and an internal grounding lug inside the compartment.

- EXECUTION

      - INSTALLATION

        - The exterior landscape lighting and street/ lighting luminaires shall be fixed to columns on the ground prior to erection. After erection of the columns and final cable connections are completed, each luminaire shall be aimed in accordance with specialist lighting supplier's instructions.

        - The lighting poles/columns shall be erected plumb. Column locations shall be staked prior to installation to assure there is no conflict with other utilities. Conflicts that arise shall be brought to the attention of the Engineer for direction in relocating column at no extra cost.

        - Foundations for pole /columns shall be based on manufacturer's data and shall be designed and detailed by the Contractor taking into account their location, corresponding soil bearing capacities and wind loads. No construction shall be done, without the approval of the Engineer.

        - Columns shall be erected onto the foundation bolts using a sling to protect the surface finish and plumb checked.

        - Control gear, located in each column, shall include a cut-out unit with sub-circuit HRC fuse rated appropriate to the luminaries(s) served and allow the use of a reduced size cable within the column where appropriate.

        - Install cabling on the head frames of the columns in weather proof tumbling of XLPE insulated copper cable. All cables shall have numbered ferrules fixed at each termination position. Other single wire cables shall be PVC insulated stranded copper of sizes to suit the number of lamps on the circuit and be installed in liquid-tight flexible or rigid galvanized steel conduits as appropriate.

      - ADJUST AND CLEAN

        - Comply with Sections 01 70 00.

        - Clean dirt and debris from all light fixture upon completion of the installation.

        - Protect installed lighting poles/columns and lighting fixtures from damage during remainder of construction period.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - Upon completion of installation of floodlights, and after building circuitry has been energized, apply electrical energy to demonstrate capability and compliance with requirements. Where possible, correct malfunctioning units at site, then retest to demonstrate compliance; otherwise, remove and replace with new units and proceed with retesting.

        - At the time of Substantial Completion, replace lamps in floodlights which are observed to be noticeably dimmed after Contractor's use and tested.

        - Check and record actual illumination levels and compare them with the design requirements as per applicable standards.

      - EARTHING

        - Throughout each installation, all conduit, trunking and metallic sheating of cables shall be electrically continuous to form a complete bonded system with the column earthing system.

        - Each column shall be connected to the earthing system by a stranded bare or PVC insulated copper wire as shown on the Drawings.

- END OF SECTION