- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Enclosed Transfer Switches including, but not limited to, the following:

            - Manual transfer switch.

            - Automatic transfer switch.

      - REFERENCES

        - BS	British Standards.

        - IEC 947-6-1	Automatic Transfer Switching Equipment (BS EN 60947-6-1).

        - Local Codes, Standards and Regulations.

      - SUBMITTALS

        - Provide catalog sheets and manufacturer’s data showing voltage, switch size, ratings and size of switching and over current protective devices, operating logic, short circuit ratings, dimensions, and enclosure details.

        - Submit manufacturer's installation instructions, application conditions and limitations of use stipulated by product testing agency. Include instructions for storage, handling, protection, examination, preparation, installation, and starting of product.

        - Submit single-line diagram of each transfer switch assembly schematic and wiring diagram of the unit.  Operating instructions for the transfer switch shall be located as required by BS EN 60947-6-1.

        - Submit factory test reports verifying that the enclosed transfer switches have successfully passed all routine tests.  Type tests results shall be submitted, when required by the Engineer.

        - It's the contractor's responsibility to get the proposed systems’ approvals without any extra time extension.

      - QUALIFICATIONS

        - Manufacturer:	Company specializing in manufacturing the Products specified in this section with minimum ten years documented experience.

        - Supplier: Authorized distributor of specified manufacturer with minimum five years documented experience, and with service facilities available in Jordan.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - QUALITY ASSURANCE

        - Except where detailed in specifications, all types of enclosed transfer switches shall comply with the requirements of Local Standards, BS and IEC.

      - OPERATION AND MAINTENANCE DATA

        - Operation Data: Include instructions for operating equipment. Include instructions for operating equipment under emergency conditions when engine generator is running.

        - Maintenance Data: Include routine preventative maintenance and

        - Lubrication schedule.

        - List special tools, maintenance materials, and replacement parts.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver, store, protect and handle products to site under provision of Section 01 60 00 – Product Requirements.

        - Store in a clean, dry space. Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect units from dirt, water, construction debris, and traffic.

        - Handle in accordance with manufacturer's written instructions. Lift only with lugs provided for the purpose. Handle carefully to avoid damage to internal components, enclosure and finish.

      - FIELD MEASUREMENTS

        - Verify that field measurements are as indicated on shop drawings.

      - MAINTENANCE MATERIALS

        - Provide one of each special tool required for maintenance.

        - Provide two lamps and fuses for each automatic transfer switch.

      - SPARE PARTS

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Fuses: 5 % of each type and rating used but no less than six. Include spares for future transformers, control power circuits, and fusible devices.

          - Indicating Lights: 5 % of each type installed but no less than six.

          - Touchup Paint: Three containers of paint matching enclosure finish, each 250 mL.

          - Furnish one set of operating coil, auxiliary contacts, auxiliary cut off contacts, etc : Six of each type.

          - Protection relays: one of each type.

        - Maintenance Tools: Furnish tools and miscellaneous items required
ATS test, inspection, maintenance, and operation. Include the following:

          - Fuse-handling tool.

          - Extension rails, lifting device, transport or dock able dolly or mobile lift, and all other items necessary to remove circuit breaker from housing and transport to remote location.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - Transfer switches shall be suitable for satisfactory and prolonged performance under the minimum/maximum ambient conditions and altitude mentioned elsewhere in this specifications.

        - All the transfer switches specified herein shall comply with the requirements of IEC 947-6-1 (equivalent to BS EN 60947-6-1).

        - Nameplates for the enclosed transfer switches shall be made from a corrosion-resistant metal with not less than 10 mm tall raised or engraved characters.  The nameplate shall be mounted to the front of the enclosure.

      - AUTOMATIC TRANSFER SWITCH

        - Automatic transfer switch shall be suitable for use as service equipment and provided as shown on the Drawings.

        - Automatic transfer switch shall be configured as electrically operated, mechanically held transfer switch with enclosure having gray enamel finish.

        - Automatic transfer switch shall be adequately rated for the application indicated and shall have the following minimum characteristics:

          - Voltage:  400 V AC.

          - Phases / Wires:  Three phase, four wires.

          - Frequency:  50 Hz.

          - Switched Poles:  Four.

          - Type of Load:  As shown on the Drawings.

          - Continuous Phase or Main Current Rating:  Not less than 125 % of the full load rating of the emergency power source.

          - Fault Current Withstand Rating:  Rated to withstand the available fault or short-circuit current available, for the duration of cycles which the current is available for before being cleared by a protective device voltage of 400 V AC.

          - Overload Rating:  As required or shown on the Drawings.

          - Main and Neutral Contacts:  Contacts shall have silver composition and be protected by approved arcing contacts for transfer switches having 400 A and larger current rating.  Neutral contacts shall have the same continuous current rating as the main or phase contacts.

        - Time delay to override monitored source deviation shall be adjustable from 0.5 to 15 seconds and factory set at 1 second.  The device shall detect and respond to a sustained voltage drop of 30 % of nominal voltage between any two of the normal supply conductors and initiate transfer action to the emergency source and start the engine-driven generator set after the set time period.  The pickup voltage shall be adjustable between 90 and 100 % of nominal and factory set 90 %.  The dropout voltage shall be adjustable from 70 to 90 % of the pickup value, and factory set at 70 % of nominal voltage.

        - Time delay before transfer to the emergency power source shall be adjustable from 0 to 5 minutes and factory set as recommended by the manufacturer and in accordance with NFPA 70 for each transfer switch.  The device shall monitor the frequency and voltage of the emergency power source and transfer when frequency and voltage is stabilized at or above 90 % of rated values.  The pickup voltage shall be adjustable from 85 to 100 % of nominal, and factory set at 90 %.  The pickup frequency shall be adjustable from 90 to 100 % of nominal and factory set at 90 %.

        - Time delay before return transfer to the normal power source shall be adjustable from 0 to 30 minutes and factory set at 30 minutes.  The time delay shall be automatically defeated upon loss or sustained undervoltage of the emergency power source, provided that the normal supply has been restored.  Transfer back to normal power shall be made "in phase" or via a timed delay transfer in the unconnected position.

        - Two normally open and two normally closed auxiliary transfer switches shall operate when the transfer switch is connected to the normal power source, and two normally open and two normally closed switches shall operate when the transfer switch is connected to the emergency power source.

        - The ATS shall also be furnished with the following:

          - Engine start contact.

          - Alternate source monitor.

          - Test switch.

          - Close differential protection.

          - Time delay by-pass switch.

          - Manual return-to-normal switch.

        - A manual operator shall be provided to permit manual operation of the ATS without opening the ATS enclosure, and incorporate features to prevent operation by other than authorized and qualified personnel.  The ATS shall be designed for use of the manual operator under no load conditions in the usual instances, but with the capability of operation under load conditions when necessary.

        - The override switch shall by-pass automatic transfer controls so the transfer switch will transfer and remain connected to the emergency power source, regardless of the conditions of the normal power source.  If the emergency source fails and the normal source is available, the transfer switch shall automatically retransfer to the normal source.

        - A green indicating light shall supervise the normal power source and shall have a nameplate engraved NORMAL.

        - A red indicating light shall supervise the emergency power source and shall have a nameplate engraved EMERGENCY.

      - PRODUCT FEATURES

        - Indicating Lights:  Mount in cover of enclosure to indicate normal source available, alternate source available, and switch position.

        - Test Switch:  Mount in cover of enclosure to simulate failure of normal source.

        - Return to Normal Switch:  Mount in cover of enclosure to initiate manual transfer from alternate to normal source.

        - Transfer Switch Auxiliary Contacts:  normally open, normally closed.

        - Normal Source Monitor:  Monitor each line of normal source voltage and frequency; initiate transfer when voltage drops below 85 % or frequency varies more than 3 % from rated nominal value.

        - Alternate Source Monitor:  Monitor alternative source voltage and frequency; inhibit transfer when voltage is below 85 % or frequency varies more than 3 % from rated nominal value.

        - In-Phase Monitor:  Inhibit transfer until source and load are within 15 electrical degrees.

        - Switched Neutral:  Overlapping contacts.

      - FACTORY TESTING

        - The factory testing shall be carried out on all types of the completed enclosed transfer switches to be supplied for the project.  Overload, endurance and temperature tests shall be conducted in that sequence and within the shortest practicable period of time on the same transfer switch without its de-energization.  The test sequence listed below shall be followed for all the enclosed transfer switches supplied:

          - General (as per manufacturer’s standard procedure).

          - Normal Operation.

          - Overvoltage.

          - Undervoltage.

          - Overload.

          - Endurance.

          - Temperature Rise.

          - Dielectric Voltage – Withstand.

          - Contact Opening.

          - Dielectric Voltage - Withstand (Repeated).

          - Withstand.

          - Instrumentation and Calibration of High Capacity Circuits.

          - Closings.

          - Dielectric Voltage - Withstand (Repeated).

          - Strength of Insulating Base and Support.

        - Wiring of each control panel shall be subjected to voltage surge tests as stipulated in IEEE C37.90.1.

        - Tests shall be performed and shall demonstrate that the operational sequence of each transfer switch unit conforms to the requirements of the specifications with regard to operating transfer time, voltage, and frequency and timing intervals.

- EXECUTION

      - INSPECTION

        - Verify that surface is suitable for transfer switch installation.

        - Verify that the site measurements are matching with the space requirements for installation, operation and maintenance of equipment.

      - INSTALLATION

        - Enclosed Transfer Switches shall be installed in compliance with the installation requirements of LV Power Distribution Boards given in Section 26 24 13 and in accordance with approved manufacturer's instructions.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - Prior to energization of Transfer Switches, check with earth resistance tester, phase-to-phase and phase-to-earth insulation resistance levels to ensure requirements are fulfilled.

        - Tests shall be performed to demonstrate that the operational sequence of each enclosed transfer switch unit conforms to the requirements of specifications with regard to various transfer timings, voltage, frequency and other characteristics in manual and automatic modes as well as normal, emergency and by-pass modes of operation.

        - All the settings and adjustments available with the Enclosed Transfer Switches shall be finally adjusted according to the control sequence in accordance with emergency power source and load priority schedules.

      - TRAINING

        - Provide instruction and training to the Owner’s staff for the operation and maintenance of the equipment. Provide a minimum of 12 hours training to be divided between classroom and hands-on training as required by the Owner.

- END OF SECTION