- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - System Includes:

          - This section describes the basic requirements for the supply, installation, testing and commissioning of fully operational Access Control- System, for the Project.

          - The systems are to be supplied with all equipment, hardware, software, cabling and ancillary services as required to provide integrated systems complete and functional in all respects, either to match the existing but with the latest models or compatible latest models to be interfaced with the existing system

          - Supply of all equipment, software and cables as required to make fully operable Access Control system, in accordance with the specifications, BOQ and drawings issued with this Contract document.

          - Installation of equipment; the Contractor has the option to sub-contract installation works to the MEP sub-contractor or an approved specialist.

          - Termination and testing of cables. Testing and Commissioning of the system including all programming and configurations.

          - Interface with other systems as detailed in this specifications and related sections.

          - Providing all the software and hardware tools to properly operate and maintain the system.

          - Technical Training to Clients Maintenance personnel.

          - Coordination with specialist Suppliers of other systems specified to be integrated with this system; Structure cabling, Computer Network Equipment, BMS, Fire Alarm System, Elevators, IPCCTV system, and with door Suppliers for installation of door hardware.

          - Gate barriers, luggage and persons scanning devices.

          - Documentation as specified.

          - Warranty services for the complete system from substantial completion.

      - REFERENCE STANDARDS

        - Contractor shall propose seamless integration with open industry protocols and related systems’ APIs, such as the integration between surveillance systems, access control, fire alarms and BMS. Security systems should be certified by internationally recognized associations such as the Open Network Video Interface Forum (ONVIF), Physical Security Interoperability Alliance (PSIA) British Standards Institution (BSI), Electronic Industries Alliance (EIA), and ISO Physical & Environmental Security.

        - B.S.

        - Local Codes, Standards and Regulations

        - All equipment and systems installed under this Contract shall meet following specifications on electromagnetic compatibility:

          - Interference immunity according to BS EN 61000: Part 6-3

          - Emitted interference according to BS EN 61000: Part 6-2

      - SYSTEMS DESCRIPTION

        - The Access Control systems shall be in line with appropriate local and international standards and in accordance with the technical and performance criteria set out in this document.

        - The Access Control system shall restrict entry to secured areas as indicated in drawings for persons authorized for these areas. The system shall be used as well for recording time attendance of employees as well as for Guard Tour live tracking, recording and management.

        - The Access Control System shall be based on distributed intelligence. Normal access control decisions shall be made at the intelligent system controllers without reference to the host.

        - In the event of failure in the communication link between an access control sub- system panel and the server computer, the access control sub- system shall be capable of buffering a minimum of 10000 access transactions until communication is re-established with the server computer. The local time schedules shall be uploaded to the server computer once the communication is resumed.

        - The security specialist shall be responsible for all door hardware required for the operation of the access control system and shall coordinate with door Suppliers to ensure that necessary provisions are made in the door frame prior to its fabrication.

        - Access Control System shall be interfaced and linked to other security systems (CCTV system,,…) as well as to the BMS/ and to the Fire Alarm System.

        - The Access Control System shall be interfaced with the control systems of elevators as shown on drawings for their control through card reader units.

        - Security system specialist shall coordinate with structured cabling.

        - Client Expectation: The contractor shall provide a method statement for each of the system performance criteria to illustrate how these requirements will be met for each of the equipment / materials being proposed.

      - SUBMITTAL

        - Company Profile.

        - Experience/ Commitments:

          - Similar work experience of installing access Control systems: The bidder shall illustrate the references of Access Control systems projects to prove his capabilities and experiences in designing, supplying, installing, testing, commissioning, maintaining, and supporting the systems, and supporting the client in any requirements needed post-project handover. This should include case studies describing the following:

            - Case Study Reference Number.

            - Project Name.

            - Client Name.

            - Project Location.

            - Project Value.

            - Project Duration.

            - Scope of Work.

            - Customer Support.

            - Challenges & Lessons Learnt.

          - Minimum of one case study shall be presented for each of the below, following the above format:

            - Experience in similar development segment (i.e. Hospitals, Hotels, retail, mixed-use, residential, etc.).

            - Experience in providing fully integrated solutions of Access Control systems.

            - Experience in enhancing Access Control systems.

          - Current commitments/ obligations: The bidder shall present all current commitments and obligations in the following format:

            - Project Name.

            - Client Name.

            - Project Location.

            - Project Duration and Target Start & End Dates.

            - Scope of Work.

          - Confirmation to having fully equipped & staffed local administration office & Engineering service center.

          - Confirmation to having local service center.

          - Other supporting information that adds value to the proposal.

        - Strategy for QA/QC:

          - QA/QC approach/procedure documents: The bidder shall provide a detailed description of QA/QC policies, method statements, procedures, people, resources, and forms used to manage Access Control systems design &/or installation projects.

          - Testing procedures: The bidder shall provide a detailed description of testing policies, method statements, procedures, program, people, resources, forms and sub-contractors used to manage each of the following testing procedures.

            - Factory acceptance tests (FAT).

            - Pre-installation tests.

            - Site acceptance tests (SAT).

            - User tests and user-defined customization.

            - 3rd party tests to be provided by both the vendors and Main Contractor, MEP contractor or project management consultant.

          - Commissioning of works: The bidder shall provide a detailed description of commissioning of works’ method statements, procedures, program, and forms.

          - Completion & acceptance certificate: The bidder shall provide the certificate forms that would be issued for completion of works and acceptance of works. The forms should include a list of statements to any additional matters and/or concerns that have been raised as part of the works.

          - Examples of installation & record drawings: The bidder shall provide an example of Access Control systems installation and record Drawings generated for a similar project.

          - O&M Manuals: The bidder shall provide an example of O&M Manuals generated for a similar project.

          - Software used to define optimal position of Access Control systems components:

          - The bidder shall provide a detailed description of the software used to define the optimal position of the Access Control systems components by analyzing aspects such as coverage areas, low vs. high density areas, etc....

          - QA-ISO 9001:2008 registration or equivalent.

          - Other supporting information that adds value to the proposal.

        - Site Survey: Site visit declaration.

        - Functional Analysis: The analysis should comply with all the requirements set in the Contract and with local authorities. Outcome of analysis should include:

          - Access control requirements in the development, defining who will be granted access to each access control reader.

          - Objective, functionality, and surveillance requirements of Security Management Application.

          - Other supporting information that adds value to the proposal.

        - System layouts and wiring drawings and diagrams including:

          - Layout drawings of entire system including containment layouts.

          - Sectional drawings of entire system.

          - Schematic diagram for entire system.

          - Layout drawing of the Secured Cabinet.

          - Power Distribution Drawing.

          - Layouts for Access Control system control rooms and equipment rooms– distances from Access Control system devices to and across these rooms.

          - Layout for power supply from main supply room and distribution boards across the Access Control system components.

          - Functionalities and snapshots of Access Control system Management software application.

          - Other supporting information that adds value to the proposal.

        - Technical Details.

          - Detailed description of proposed solution:

            - Type and topology of access control proposed.

            - Number and locations of access control readers.

            - Types of access control readers and specifications (card, code pad, IP rating, manual override, etc.).

            - Outdoor/Indoor requirements.

            - Space in server racks available in main security room.

            - Technical data sheets of all equipment, software and materials.

          - All civil, MEP and support works, including and not limited to:

            - Containment.

            - Cabling.

            - Scaffolding and access ladders.

            - Labor.

            - Power supply.

            - Other tools & services.

          - Unless advised otherwise, contractor is self-supportive and should include for his offer his own materials, tool, services, office, and any requirement necessary to complete this project.

          - Provide samples of all types of proposed system’s devices, fittings, accessories,..etc. together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

          - Coordination with other parties.

            - Method statement.

            - Scope of work matrix for all works listed in this Contract Deliverables Section.

            - Communication protocol.

          - Outline risk assessment for all major aspects of the works.

          - General method statement/risk assessment on approach to day to day responsibilities.

          - List of Spare parts to be provided for minimum 10 years.

          - Item by Item commentary on technical requirements.

          - The Contractor shall comply with all specifications described in the Technical Specification sections herein. System specifications proposed should reflect each of the system components in question, functionality desired by the system component and the how the component integrates with the centralized system. The contractor shall add 3 columns beside each item to state the following:

            - First column is ‘Bidder’s Compliance’:

              - Contractor shall specify here one of the below:

                - Y: proposal does comply with specification/requirement.

                - N: proposal does not comply with specification/requirement.

                - N/F: proposal does not fully comply with specification/requirement.

                - N/A: specification/requirement is not applicable to the project.

            - Second column is ‘Reference’:

              - Contractor shall refer each compliant item to the related section of proposal, such as CCTV, Fire Alarm systems,… etc.

              - Component data sheet or reflected electrical/ceiling/wall plans layout drawing.

            - Third column is ‘Bidder’s Comments’:

              - Contractor shall note down any further description, comment, feedback, concern, etc. on each item.

              - Contractor shall note down any further description, comment, feedback, concern, etc on each item.

          - Vendor certificates.

            - Company certification by vendor as authorized dealer.

            - Personnel certificate by vendor as factory-trained.

            - Product quality assurance certification by vendor.

          - Vendor list and selection criteria for all items, vendors should adhere to the following criteria:

            - Company established at least 10 years ago.

            - Have references of at least 20 projects globally of similar scope & complexity.

            - Based in JOR or neighboring countries since at least 5 years.

            - Have references of at least 5 projects in JOR or neighboring countries of similar scope & complexity.

            - Have a local support office.

            - Have a local warehouse for spare parts stocking.

          - Proposed subcontractors identified and scope of work for each.

          - Confirmation of guarantee periods for equipment and guarantee terms & conditions.

          - Confirmation of warranty periods for equipment and guarantee terms & conditions.

          - Maintenance & support offering – sufficient details.

          - Other supporting information that adds value to the proposal.

        - Bidder’s Compliance Letters.

          - Conformity of bid to requirements – sufficient technical details.

          - Conformity to agree on Confidentiality Agreement.

          - Letter of Bidder’s Compliance with All Specifications.

          - Conformity of responsibility to secure Compliance with related government/utility authority.

        - List of Proposed Personnel with CVs & Responsibility Matrix.

          - Relevant experience for key team members.

          - Other supporting information that adds value to the proposal.

        - Schedule of Works: Bidder shall compile a schedule of works and include a project milestone as per Master Schedule of Works provided. It is up to the bidder to create a schedule that best incorporates all works.

        - Handover & Close-Out Documentation.

          - As Built Drawings.

          - End User Manuals.

          - Maintenance Manual.

          - Operations Manual.

          - Plans as mentioned above.

          - S/W license, update and upgrade procedures.

          - Other supporting information that adds value to the proposal.

        - Shop drawings and catalog data submittals shall be made in accordance with relevant sections. The Contractor shall submit sufficient information to indicate the scope and quality of the Access Control system installation.

          - Block diagram showing system relationships of major components and quantities and interconnecting cable requirements.

          - Plans showing equipment locations, conduit, and conductor requirements.

          - Control console and panel arrangements, equipment outlet devices, and special mounting details.

          - Wiring diagrams showing terminal identification for field-installed wiring.

          - Catalog literatures with system equipment specifications.

          - Spare parts list.

          - Method Statement for installation, testing and commissioning of the system.

        - The Contractor shall furnish operating service manuals for the system. The manuals shall be bound in flexible binders and all data contained therein shall be printed or typewritten. Each manual shall include all instruction necessary for proper operation and receiving of the system, and a complete block diagram of the system, a complete circuit diagnosis of the system, and a wiring designation schedule for the camera, as well as other major components, and a replacement parts list.

        - The Contractor shall meet all project requirements, yet he is required to submit to the Engineer for his approval a proposal for an upto date technology system.

        - Workshop Drawings

          - Lay out drawings complete with cable sizing, cable routing, containment sizing, location of equipment, power requirements and data ports for system components, etc and installation details of door hardware. Drawings shall also indicate requirements of back boxes, pull boxes, panels, data, power, control wiring… etc. The above information shall be provided to the MEP contractor on time as per the project program for providing containment and builder's works, and to the door Suppliers for manufacturing doors with all provisions as required by the specialist.

          - Controller and Matrix wiring diagram clearly showing power, data and similar requirements.

        - As-Built Drawings: Submit number of sets of final as-built drawings as indicated in the contract documents including the above items marked up with labels of each component.

        - Operation & Maintenance Manual:

          - Descriptive data of all operating, user and application software including complete operators manuals, programmers manuals, and alphanumeric point name convention sheet.

          - Provide final documentation to serve the diverse needs of personnel concerned with operation, procurement, installation and maintenance.

          - Operation & Maintenance manuals shall be complete with preventive maintenance schedules, procedures and troubleshooting procedures.

        - Training Manual: Shall be provided to client’s staff and shall include brief description of the installed system, preventive and breakdown maintenance procedures and training mode.

      - QUALIFICATIONS

        - Access Control System components shall be manufactured by firms that are regularly engaged in the production of Access control system, and auxiliary equipment similar to that required for this project and that have been satisfactory service for at least 10 years.

        - The firm installing the Access Control system shall have had a minimum of 5 years documented prior successful installation experience with Access Control systems similar in scope to the system of this project.

        - The system shall be engineered, commissioned and serviced by the manufacturer or manufacturer's authorized systems integrator employing factory trained personnel for commissioning and after sales support. Materials and equipment shall be the catalogued products of manufacturers regularly engaged in production of Access Control System (ACS). The proposed products shall be the latest versions commercially available at the time of the bid.

        - The manufacturer shall be ISO-9002 and ISO 9001 certified for Quality Assurance in Production, Installation and Servicing.

        - The systems integrator shall be an authorized partner to the manufacturer and the partnership shall be at least two year old. The manufacturer systems integrator combination shall have successfully implemented at least three projects of similar complexity.

        - The specialist shall obtain and submit a written undertaking from the manufacturer that the spare parts of the system proposed will be made available upon request for at least 10 years from the date of substantial completion. In addition, the manufacturer shall undertake to ensure forward compatibility of the proposed equipment for at least 15 years.

      - QUALITY ASSURANCE

        - The Contractor shall post a note, at the accesses control device, to indicate the name, address, and telephone number of the firm to call when service is necessary.  Note shall be mounted in a metal frame attached to the device case.

        - Operation of the Access Control system shall be demonstrated to the Engineer to prove, under normal conditions, that coverage complies with this specification.

        - Reference Demonstration: System Integrators would be asked to demonstrate a working Access Control system as per the document specifications to prove their ability to comply with Project requirements. The proof-of-concept  demonstration  of  the proposed Access Control system shall be as follows:

          - Location: Access Control system / command center reference site using a solution proposed by the System Integrator.

          - Configuration: The installed solution is expected to be exposed as much as possible for physical examination.

          - Real-Time Demonstration:

            - The integration of all components specified in this document should be demonstrated in real-time as a working system. More references could be used to demonstrate different components, depending on the projects’ scope.

            - Demonstration of events, alerts, reporting, scheduling of events, Management application and other possible functions of the Access Control system are required.

      - PRE-INSTALLATION MEETINGS

        - Convene minimum one week prior to commencing work of this section.

        - Conform to manufacturer’s standard service conditions during and after installation of components.

      - FIELD MEASUREMENTS

        - Verify field measurements prior to fabrication.

      - SPARE PARTS

        - Supply as maintenance stock, consumable devices, components as recommended by Supplier including additional (spare) card readers, ID cards, access control tags, break glass units, magnetic cells, electromagnetic locks, ..etc),    but shouldn’t be less than two units of each type/ rating of installed consumable material/ component/ device, incase less than three numbers of devices/ material are installed, minimum of one unit of each type/ size/ rating of each device/ material shall be provided as spare stock.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide (12) months full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of (1) year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Three Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and software and hardware administration of the system without or with minimal assistance from the vendor’s technical staff.

        - Engage a factory-authorized service representative, whose credentials are approved by the engineer, to explain programming and operation of systems and to train Employer's maintenance personnel on procedures and schedules for maintaining, programming, operating, adjusting, troubleshooting, and servicing system.

        - Training shall be carried out to an approved training manual Separate training shall be provided on the hardware and software. Each training shall have both class room session and hands on session. Contractor shall allow for 6 trainees each in both the trainings.

- PRODUCTS

      - GENERAL

        - Access control system products shall meet or exceed the following specifications. It is the responsibility of the specialist contractor to add any product for which specifications are not provided but require for the smooth operation of the system.

      - MANAGEMENT SOFTWARE

        - The management software shall allow control and monitor of access and security to the project. The software shall allow centralized alarming, card holder management etc. and shall have comprehensive reporting capabilities – standard and customized.

        - The system shall also support Photo ID badging and Time Attendance.

        - The Management system shall use a Client Server architecture based around a modular PC network, utilizing industry standard operating systems, networks and protocols.

        - The system shall allow the distribution of system functions such as monitoring and control and graphical user interface etc. across the network to allow maximum flexibility and performance. The architecture shall include support of various Wide Area Networks using standard hardware and software to link nodes into a single integrated system. The network protocol used shall be industry standard TCP/IP.

      - DATABASE

        - The system shall store security related cardholder information in a relational database.

        - The cardholder database shall support at least 1000 cardholders. The cardholder database shall be delivered with at least 40 user definable fields for storing data specific to the requirements of different systems. It shall be possible to increase or decrease this number of user definable fields. Systems without the ability to increase the number of user definable fields shall not be accepted.

        - It shall be possible to define labels and field types for each of the user definable fields. It shall be possible to define lists of choices for certain user fields to avoid unnecessary typing, for example, defining a list of department names. It shall also be possible to modify the layout of cardholder fields on the display screen to alter the look to particular user’s requirements. It shall also be possible to create more complicated calculations between user fields. For example, creating the value of one user field based on the value of two others. It shall be possible to define default values for all user fields, which shall be applied when the cardholder is first added to the system.

        - Searching and Sorting: It shall be possible to define which user fields in the cardholder database are searchable fields. All searchable fields shall be able to be used to call up a list of cardholders who match a certain criteria. In addition, it shall be possible to search on multiple cardholder characteristics at one time, for example, all cardholders in department “X” who have a supervisor of “Y”. A list of matching cardholders shall be displayed and an appropriate choice may be made.

        - Multi-selection: It shall be possible for multiple cardholders to be selected and a single edit to be performed on all of these cardholders selected. For example, it shall be possible to select all cardholders in department “X” and change their address to “Z” in a single operation.

        - Templates: The system shall define templates in order to add groups of cardholders with predefined characteristics. A template shall contain all the relevant details for a particular group of cardholders such as all their user fields and access levels. When adding a new cardholder to this group using the template, the cardholder shall be added with the same characteristics as defined in the template.

        - Cardholders and Cards:

          - It shall be possible to assign a single cardholder multiple cards for use in the system. Multiple cards assigned to a single cardholder shall be able to be in different states. For example, it shall be possible for a single cardholder to have both an “active” card assigned and an “inactive”, “lost” or “stolen” card assigned.

          - It shall also be possible to support different technologies of access control cards in the one system. For example, a single cardholder may have a proximity card, a magnetic stripe card and a biometric template assigned to them.

          - Cards may be created and assigned to cardholders separately. It shall be possible to “return” a card when a cardholder no longer requires it, and then reassign it to another cardholder without having to delete and recreate the card.

          - When cardholders or cards are deleted or expired, or when a card is returned from use by a cardholder, the system shall automatically download this to the field controllers so that these cards no longer provide access.

        - Access Permissions, Time Periods and Zones:

          - Time Periods

            - The system shall support a minimum of 256 time periods.

            - The operator shall be able to access a summary display listing all time periods and their descriptions. From this display the operator shall, if the operator is configured for the time period’s area code, be able to go to a time period detail display showing the time periods configurable parameters.

            - Once the changes have been saved, the operator will be required to download the new data before it is enabled in the Access Control system. This shall allow operators to make a number of changes but only be required to download once.

            - Each time period detail display containing changed data that has not been downloaded shall clearly indicate this to the operator via a flashing warning message. Download of this data shall cause the warning message to disappear.

          - Zones

            - The system shall support up to 1024 zones. Each zone shall consist of the following:

              - Description

              - Area code.

              - Up to 128 card readers or floor points.

            - The operator shall be able to access a summary display listing all zones and their descriptions. From this display the operator shall, if the operator is configured for the zones area code, be able to go to a zone detail display showing the zone configurable parameters.

            - Zones shall be automatically created when card readers are configured in the system. Zones are defined by the card readers, which allow entry to the physical space, which the zone represents. One reader may only be defined as entering one zone. Each reader will indicate the zone it allows entry to and optionally the zone from which one has exited.

          - Access Permissions

            - The system shall support up to 1024 access permissions. Each access permission shall consist of the following:

              - Description

              - Area code.

              - Up to 256 zone and time period pairs.

            - The operator shall be able to access a summary display listing all access permissions and their descriptions. From this display the operator shall, if the operator is configured for the access permission's area code, be able to go to an access permission detail display showing the access permission's configurable parameters.

            - Once the changes have been saved, the operator will be required to download the new data before it is enabled in the Access Control system. This shall allow operators to make a number of changes but only be required to download once.

            - Each access permission detail display containing changed data that has not been downloaded shall clearly indicate this to the operator via a flashing warning message. Download of this data shall cause the warning message to disappear.

        - Security

          - Managing cardholders shall only be available to operators who are at a certain security level. Both cardholders and cards shall also confirm to standard system Operator Security features such as area assignment as defined in this section.

          - It shall be possible to define an operator as only a cardholder administrator. All other functions in the system will be restricted to this operator except for cardholder administration functions.

        - Assigning Access to Cardholders: Cardholders may have up to 8 different access levels assigned to them. Each of these access levels may define a separate set of readers and times that will allow the cardholder access. Operators shall be presented with a list of all access levels already assigned to the cardholder and all access levels that are currently unassigned.

        - Deleting Cardholders: Cardholders may be deleted but retained in the database for future reference if required. It shall then be possible to “undelete” the cardholder should this be required. It shall also be possible to permanently delete the cardholder record in order to prevent unnecessarily large databases from developing.

        - Card/Cardholder Expiry:

          - Cardholder and card expiry dates may be defined down to a resolution of date and time in minutes.

          - It shall be possible to assign cardholders and cards separate expiry dates, enabling a card assigned to a cardholder to expire before the cardholder expires. However, it shall not be possible for the card expiry date to exceed the cardholder expiry date of the cardholder to which a card is assigned.

          - Expiry dates may be set up by default to be a particular given date, or a relative period from the time the cardholder was created (e.g. 1 year).

          - It shall be possible to assign a cardholder a commencement date and have their assigned cards automatically become active on this commencement date.

        - Cardholder alarms: It shall be possible to specify that the cardholder generate an alarm when they use their card. This setting may override the alarm setting of the reader to which a cardholder may be presenting their card.

        - Cardholder events: All changes to cardholders in the system shall be logged in the event summary and shall list the new value of the cardholder field. Similarly, any time a cardholder accesses a card reader; an event will be listed in the event summary. It shall be possible to automatically view all the events generated for a particular cardholder directly from the cardholder displays without having to run a separate report.

        - Uses before Expiry: It shall be possible to define the number of times that a cardholder may use their cards. This number shall be decremented every time the cardholder uses their card at a reader until the number is 0, when the cardholder shall no longer have access.

      - SOFTWARE FUNCTIONS

        - Event Initiated Programs

          - Physical and software outputs or groups of outputs shall be assignable through configurable algorithms to an input point. When an input changes state the outputs assigned shall be activated as specified by their physical or configured output modes.

          - When alarm events of individual or groups of points are suppressed by event initiated programs, any occurrence of such alarm events during the suppress mode shall not be enunciated, reported or journalized.

        - Event Management.

          - Events shall consist of alarms, changes of state in a monitored status point, cardholder movements, changes in system status and operator actions.

          - All journal events shall be recorded as necessary to include event description, condition, message, time of occurrence, operator responsible and any other information or tags.

        - Report Management: The system shall support a flexible reporting package to allow easy generation of report data. The reports provided shall include pre-configured standard reports for common requirements such as Alarm Event reports and custom report generation facilities that are configurable by the user.

        - Standard Reports: The following pre-formatted reports shall be available on the system:

          - Door History

          - Group Card Trail

          - Cardholder List

          - Occupancy

          - Access Data Import/Export

          - Card Usage

          - Access Permissions

          - Time Period

          - Zone Information

          - Cardholder Details

          - Cardholder Zone

        - Door History Report: A report shall be provided to list all cardholders who presented a card at any specified door or group of doors monitored by the system within a specified time period. The time period may be specified as an absolute start and end date and time, or as a period relative to the current time. The report shall contain the time and date and card number for each card presentation.

        - Group Card Trail Report: A report shall be provided so that when requested, the report shall search the database for cards corresponding to specified search criteria based on any cardholder field. It shall then show all doors accessed by these cardholders in a specified time period. The time period may be specified as an absolute start and end time, or as a period previous to the current time.  The report shall contain the date and time of access and the point identifier of each door accessed.

        - Cardholder List Report

          - A report shall be provided to produce a comprehensive listing of cards and cardholders.

          - It shall be possible to provide searching and filtering criteria based on any cardholder field. The cardholder details on which the report is based shall allow details to be specified as a range, or as matching or partially matching as applicable.

        - Occupancy Report: A report shall be provided so that when requested, the report shall determine which cardholders are in a specified zone at that time. Listing the Doors accessing the area for both the IN and OUT directions shall specify the area. It shall be possible to include only certain cardholders in this report, as defined by the specified search criteria based on any cardholder fields.

        - Access Data Import/Export Report: A report shall be provided to create a file containing cardholder related details in an ASCII format ready to be exported from the System into a third party database package. It shall also be possible to import ASCII files into the system to update the system from information from other third party database systems. The following information shall be able to be configured for import or export in the report:

          - Cardholder Details

          - Zones

          - Time periods

          - Access permissions

          - In order to reduce duplication and report file size, the operator shall be able to choose to only include cardholders that have been modified since a particular date.

          - It shall be possible to configure the report such that after an import operation, a download to the field devices shall take place automatically.

        - Card Usage Report: A report shall be provided which calculates the total number of access movements (including no movements) for cardholders over a given period of time. The time period may be specified as an absolute start and end date and time, or as a period relative to the current time. This report shall provide the ability to search by cardholder fields as defined by the specified search criteria based on any cardholder field.

        - Access Permissions, Zone, and Time Period Information Reports: A number of reports shall be provided which lists configuration information for access permissions, zones and time periods. These reports shall allow the system administrator to check and confirm the configuration of the access control parts of the system.

        - Cardholder Details Report:

          - A report shall be provided to produce a comprehensive listing of cardholders that match a set of search criteria.

          - It shall be possible to provide searching and filtering criteria based on any cardholder field. The cardholder details on which the report is based shall allow details to be specified as a range, or as matching or partially matching as applicable.

        - Cardholder Zone Information Report: A report shall be provided which lists zones in the facility to which cardholders have access. This report is to allow system administrators to check which parts of their facility are accessible by which cardholders.

        - Guard Tour Tracking and management:

          - The system shall be able to provide Guard Tour Tracking and management reports.

          - The Guard Tour Live Tracking Window shall be opened automatically at the initiating monitoring station whenever a tour is launched. The Guard Tour Live Tracking Window shall consist of a series of columns including:

            - Checkpoint Sequence Number

            - Checkpoint Name

            - Checkpoint Status

            - Checkpoint Min Time

            - Checkpoint Max Time

            - Checkpoint Time (0 if status is “not reached” or “missed”)

            - The following checkpoint statuses shall be supported:

            - Checkpoint Not Reached

            - Checkpoint Reached On Time

            - Checkpoint Reached Early

            - Checkpoint Overdue

            - Checkpoint Reached Late

            - Checkpoint Out of Sequence

            - Checkpoint Missed

            - Guard Tour Initiated

            - Guard Tour Completed

            - Guard Tour Completed With Errors

            - Guard Tour Cancelled

            - Guard Tour Terminated

        - Access Control & Visitor Management Software:

          - This is an optional requirement. A server-based access control and visitor management application might be requested for certain assets which shall be specified by the Engineer.

          - Access Control & Visitor Management features should be able to interface with the card readers and ANPR system to be able to manage access of pedestrians through pedestrian gates, and access of Guests/ visitors into the community, as well as identify and register Guests/ visitor’s car number plates to allow convenient access for permanent Guests/ visitors.

      - INTELLIGENT SYSTEM CONTROLLERS

        - Intelligent system controllers shall be provided for a group of doors based on their geographical location. The Controllers shall operate on 230VAC and Ambient Operating Temperature shall be from 0°C to 60°C.

        - The controller shall be communicating to the System’s PC through Ethernet TCP/IP protocol using unique Mac address for central configuration.

        - Controller shall be modular in construction, each supporting up to 16 card readers. 25% spare shall be available in each controller.

        - Controller shall the capability to support I/O Card of 32 monitored digital input points and 16 digital output points. It shall support up to 50,000 cardholders.

        - The hardware and software of the controller shall have the capability for downloading and saving, remote Data analysis, allowing or prohibiting the access through physical aids, transferring data with other communication means and printing. In local mode, the controller shall also retain the access and alarm events (minimum 20000 events), and shall download the data to the system’s PC upon restoration of communication.

        - The unit shall be microprocessor (32 bit) based and shall include dynamic and static memories with enough capacity to cater all the required databases. The system-controlled components shall be grouped in one enclosure with power supply; self-power regulation, heat dissipation ventilators, self-protection against power failures, surges and the like. It should be capable of controlling relay outputs (number to be clarified by the manufacturer).

        - Controller shall have serial and parallel ports as well as Ethernet or TCP/IP. Communication with card readers shall be in an open communication format shall be achieved with twisted pair shielded cables of length up to 150 m.

        - Accessories shall include, but not limited to diagnostic LED for status indication (ON, OFF, FAULT), data processing flashing LED and ports status LED (TRANSFER, DISABLED, FAULT).

        - The modular multitask units shall:

          - Constantly control the status of equipments

          - Collect information

          - Send data to the system’s PC

          - Work as independent processors

          - Use a high level programming language, ensuring reliability, future extension

        - Each unit shall contain:

          - Communication interfaces,

          - Universal digital input, digital output controls,

          - Universal analog input, analog output controls,

          - A plug-in communications module for maintenance,

          - A friendly language display,

          - Built-in time reminder functions to ensure that special maintenance requirements will be steadily annunciated,

          - Self-diagnostic system,

          - Voltage switching relays

        - The central Memory Unit shall perform the following functions:

          - Connection of the programming console (directly, or via the network),

          - Running of the application program,

          - CU operating mode control,

          - Time stamp,

          - Control of 5 ms to 1 second programmable watchdog device

        - The program memory shall be in a non-volatile RAM type memory and battery safe.

      - SYSTEM’S HARDWARE

        - The system PC computer shall be to the specifications of the manufacturer, but shall have the following minimum configuration:

          - CPU:  Intel Core 2 Due, 2.2 GHz

          - RAM: 4GB HDD Space: 320 GB free space

          - O/S: Windows XP Professional

          - Monitor: 17-inch

          - DVD

          - 4 MB Video Card

          - Sound Card

          - Mouse, Keyboard

          - A tape backup unit

          - An 8-line serial communications adapter

          - An Adapter for Ethernet Networking compatible with TCP/IP network protocols

      - DOOR INTERFACE UNIT

        - Wiring from each door shall be concentrated in a junction box which may be active or passive depending on the system architecture of the selected vendor. The interface unit shall provide power for the operation of all associated active devices including electrically operated locks.

      - CARD READERS

        - Card readers shall support contactless Smart Card technology. Card readers shall support the proximity smart cards compliant with ISO 14443 A or B Standard and ISO 15693.  It shall support Card plus PIN reader and Card only reader. The reader shall include beepers, and red and green LEDs, to provide feedback to users.  A beeper shall give different beeps to indicate Access granted or Access denied. A red LED shall flash red for access denied. A green LED shall flash green for access granted and shall show solid green when there is free access. A method of LED indication shall be required to indicate if a second card is needed for escort or dual authorization modes.

        - Readers with integrated PIN pad shall have back lighting on the keypad.

        - Each reader shall be identified independently at the central control by means of a unique plain language descriptor. The central control plain language descriptor shall be at least 60 characters in length.

        - Readers must comply with at least IP54 environmental protection rating.  All outdoor readers shall have a vandal resistant enclosure to IP66 rating.

        - Any Cardholder entering an "anti-passback zone" controlled by a reader must exit from that zone by presenting their card to an exit reader.

        - The system shall include an optional “anti-passback” feature to allow Cardholders to re-enter the zone after a user-defined, pre-set time period has expired.

        - Every incorrect PIN attempt shall be notified at the central control as an alarm condition.

        - Each reader shall be capable of automatically switching the access mode at a door at different times of the day, based on control parameters received from the central control. The following access criteria modes are required:

        - Free access - Door is unlocked, no card entry required.

        - Secure access - Door is locked, a successful card attempt is required for valid entry or exit. Door re-secures after access attempt.

        - Secure + PIN access - Door is locked, a successful card and correct PIN number attempt is required for valid entry. Door re-secures after access attempt.

        - Override from reader – Members of certain access groups shall be able to change the access and PINs mode of the door at certain times.

        - Dual Authorisation - access is granted only when two different but legitimate cards are presented within a given time frame.

        - Escort – A second card is required to be presented from a cardholder who is nominated in the “Escort Access Group”.

        - Shared PIN Number – The system Operator determines what the PIN number will be and programs this into the system. Access is allowed through the door when the correct 4 digit PIN is pressed followed by the “Enter” key.

        - Cardholder access reporting to the central control and logging in the audit trail shall be configurable in two modes:

          - Only when there has been a successful presentation of a valid access card AND the door open sensor has detected that the door has actually been opened.

          - Whenever there has been a successful presentation of a valid access card irrespective of if the door has been opened.

      - ID CARDS

        - Cards shall be contactless Smart Card and shall be passive. It shall be of standard credit card size, being no larger than CR-80 and shall be direct printable using a dye-sublimation print process or be capable of accepting an adhesive label printed through such a process. All cards shall meet ISO 14443 A or B Standard and ISO 15693 standards.

        - Smart Cards shall incorporate Mifare Standard technology. The card number shall be a number specifically coded onto the card, and not a serial number.

        - Card holder database shall be stored in the smart cards.

        - During transmission of data between a proximity access token and a proximity reader, the data shall be encrypted.

        - There shall be barriers employed to prevent the deciphering of access control data stored on the card using any readily available equipment. The tenderer shall document the barriers used.

        - There shall be barriers employed to prevent the copying or altering of access control data stored on the card using any readily available equipment. The tenderer shall document the barriers used.

        - The system shall be capable of uniquely recognizing card numbers up to seven (7) digits in length.

        - The system shall be capable of uniquely recognizing and handling up to 15 issue levels for each unique Card number ID.

        - Cards shall be able to be encoded by the supplier according to the client’s specifications, made known at the time of order. Cards and tokens supplied with manufacturer determined card numbers will not be acceptable.

        - It shall be possible to encode cards to allow operation of a user defined Personal Identification Number (PIN) and the card still be supplied ex stock as defined above.

      - DOOR RELEASE BUTTONS

        - Door release buttons to comply with the following:

          - Install on the egress side of selected access controlled doors as indicated on the drawings

          - On activation, the associated door alarm will be deactivated for a period and the power interrupted, to allow travel through the door and door to close, while sending a door exit signal to the associated ACP

          - Buttons are to be dual pole with one pole signaling the ACP and the second pole kill power to the lock (if lock is fail safe)

          - Compatible with the requirements of the access control system and door locks (i.e., the device will signal a valid egress before releasing the electronic lock)

          - The centreline of the door release button will be positioned at a height equal to the centreline of the lock/latch assembly for the associated door

      - MAGNETIC REED SWITCHES

        - Flush Type

        - Flush magnetic reed switches to comply with the following:

          - Install on nominated internal and perimeter doors as indicated on the drawings

          - Diameter to be determined on site

          - Mounted in top of door jamb not side of door frame

        - Surface Type (Heavy Duty)

        - Surface magnetic reed switches to comply with the following:

          - Install on roller doors, gates as indicated on the drawings

          - Provide tamper proof junction box for cable terminations and end of line resistors

          - Position so as not to be damaged by vehicles or other traffic

          - Stainless steel armoured cable

          - Corrosion resistant

      - FIELD HARDWARE POWER SUPPLIES

        - Provide Power Supplies for field hardware, which must be compatible with the Access Control Equipment installed.

        - Power Supplies must be regulated, linear and isolated versions for the field panels and other equipment.

      - SONALERTS

        - There are two functions for sonalerts on the project.

          - For alarming on door open too long alarm (DOTL). Refer drawing for locations.

          - DOTL sonalerts must comply with the following:

            - Be located above the access controlled doors noted on the drawings

            - Sound levels adjustable from 40 dB to 110 dB

            - Sound if the door remains open longer than a predetermined period. Should the door continue to remain open longer than a second and subsequent predetermined period, only then is an alarm to be generated at the operator terminal

            - Be capable of being isolated via the operator terminal and be disabled when the associated door is in access mode

            - Be flush ceiling-mounted, complete with sound selection and level adjustment

      - DOOR LOCKING

        - Refer to the project door schedules for the type of lock required for each particular access controlled door.

        - Locks shall be supplied from power supply units – POE to the lock is allowed.

        - Mortice Locks

          - Electric mortice locks will comply with the following:

            - Switchable for either power-to-unlock (fail-secure) or power- to-lock (fail safe) with dead latch, unless otherwise specified

            - Be provided with Registered Key Manual Override

            - Monitor:

              - Key override

              - Door handle operation

              - Dead latch and door closed status (in series with reed switch)

            - Be fitted with an internal door release switch and be free handle exit (i.e., not utilising standalone door release buttons)

            - Operation of a free handle shall suppress the associated access control door alarm

        - Electric Strikes

          - Electric strikes will comply with the following:

            - Monitor dead latch pin and electric tongue sensor

            - Associated lock shall be provided with a Registered Master Key cylinder for manual override

            - Request to exit buttons fitted on secure side of nominated doors

            - Be configured for power-to-lock (fail-safe) with dead latch, unless otherwise specified

            - Tongue sensor wired in series with reed switch

        - Electronic Maglock

          - Electric maglock will comply with the following:

            - Installed within full transoms to match the associated door width type.

            - Transom to be powder coated to meet door/frame finish.

            - Instant release circuit - no residual magnetism

            - Fully sealed electronics - tamper proof and weatherproof

            - Mounted using steel machine screws into blind finishing nuts and glued

            - Architectural brushed stainless steel finish (US32D/630)

            - All ferrous metal surfaces plated to MIL specification

            - Include mounting brackets, housings and dress covers

            - Holding Force: 600 lbs. [272 Kg.]

            - Current Draw and Voltage: 300mA at 12VDC

        - Cable Transfer Unit

          - Cable transfer units will comply with the following:

            - Be recessed in the door leaf and the door frame so as to conceal all cabling

            - Be installed to all electric mortice lock doors so that cabling can transfer from the frame of the door to the door leaf

          - Exposed curly cords and the like will not be accepted.

      - CONCEALED DOOR POSITION SWITCH/MAGNETIC CONTACT

        - Application 20mm Plastic Flush, Cabled Contact for use on Steel doors.

        - Material	ABS Plastic

        - Colour	White, Brown or Gray

| - Contact Dimensions & Fixing |  |  |
| --- | --- | --- |
| 1. Depth (mm) | 25 |  |
| 2. Flange (mm) | 36 x 22.5 |  |
| 3. Body Diameter (mm) | 20 |  |
| 4. Cable Length (cm) | 100 |  |
| 5. Fixing | Screws |  |

        - Magnet Details

          - Depth (mm)                          15

          - Flange (mm)                       36 x 22.5

          - Body Diameter (mm)            20

          - Fixing                                  Screws

      - SURFACE MOUNTED DOOR POSITION SWITCH/MAGNETIC CONTACT

        - Application 100mm bushed aluminium surface mounted, Cabled Contact for use on Steel doors.

        - Sizes: 10.80cm x 3.81 cm x 1.91 cm

        - Triple biased for increased security

        - No field adjustment

        - Pry tamper included

      - BREAK GLASS UNIT (BGU)

        - The product must provide the following minimum requirements:

          - The BGU’s white plastic shall be key resettable after activation.

          - The unit shall be of the non-fracture type with spring hinged cover, coloured green and engraved “EMERGENCY DOOR RELEASE”.

          - The BGUs shall have triple pole contacts so that if activated they can both break the positive and negative supply to the adjacent door lock and be monitored by the access control system.

          - Operation of the unit shall release the associated door lock such that the door may be freely used until the BGU is reset using a reset key. The BGU shall operate directly on the lock to ensure fail- safe exit capability.

          - Break glass units shall require only finger pressure to activate.

          - The unit shall be protected by a clear plastic removable cover

          - The Security Contractor shall install a piezo sounder within the back-box of the unit and connect it so that it shall provide an audible alarm for ‘door-forced’ and ‘door-held’

      - PROXIMITY REQUEST TO EXIT (RTE)

        - The product must provide the following minimum requirements:

          - Flush mounted single gang stainless steel faceplate

          - When the RTE button is activated, the normally closed contact shall open providing a RTE command to the door controller that shall inhibit the door open alarm for a predetermined period and provide a timed release of the door lock for egress.

          - There shall be a pre-determined time period for personnel to access via the controlled door and for the door closer to operate and the lock re-engage

      - DURESS BUTTONS

        - The product must provide the following minimum requirements:

          - Duress buttons shall be deliberately operated devices requiring two separate actions before activation.

            - Mechanical latching action released/reset by a key.

            - Metal-clad construction.

            - Normally closed contacts that shall open on activation.

      - Airlock system

- 2 Door interlock for access controlled systems:

- Interlock device that prevents more than one door being open at anytime, thus creating an airlock between the inner and outer environments.

- A door interlock system requires the user to pass through two doors in sequence to

- enter the premises. The doors are monitored to ensure that they cannot both be open

- at the same time.

- The system follows the sequence:

- 1. Request to open a door.

- 2. Confirm that the other door is Closed.

- 3. Accept the door open request - Energise the Lock Out relay.

Features

- Switchable for fail safe and fail secure locks.

- Can be used as a standalone device.

- Multiple units can be connected together for scenarios where more than 2 doors need to    be interlocked

- Includes plastic casing.

- Simple to wire up.

| Electrical | Min | Max |  |
| --- | --- | --- | --- |
| Voltage | 11V DC | 15V DC |  |
| Current - Default N.O. operation |  | 75 mA |  |
| Current - Default N.C. operation |  | 150 mA |  |
| Lock relay voltage |  | 24V DC |  |
| Lock relay current |  | 4A |  |
| Lock relay lifetime | 100,000 operations |  | at 24V DC, 4A |
| Environment |  |  |  |
| Operating temperature | 0 °C | +55 °C |  |
| Waterproof |  |  | Indoor use only |
| Dimensions | Width | Depth | Height |
| Control Unit | 70 mm | 70 mm | 25 mm |
| Plastic Cabinet | 120 mm | 120 mm | 40 mm |

- EXECUTION

      - SUPERVISION

        - All works associated with implementation of the security ACS shall be carried out under the direct supervision of a representative of the approved specialist systems integrator. Installations shall be carried out by skilled technicians.

      - WORKSHOP DRAWINGS

        - Detailed engineering shall be the carried out by a factory trained engineer working with the approved specialist systems integrator. Workshop drawings shall detail all cable types, conduits, backbox / power requirements, mounting details etc.

        - Workshop drawings submitted for the engineer’s approval shall be duly signed and stamped by the specialist systems integrator.

        - Detailed system schematic diagram showing cable sizes and types, exact locations of devices, PC etc. shall be submitted along with the workshop drawings.

      - COORDINATION

        - The supervisor of installation shall be fully responsible for coordination with specialist integrators of other systems to which the system has an interface or integration.

      - LABELING

        - A labeling scheme shall be submitted for approval of the engineer. All cables and devices shall be labeled to the approved scheme.

      - CONTAINMENT

        - All wires and cable shall be installed in metallic cable trays or concealed rigid PVC conduits as shown on drawings. Sizing of containment shall be carried out during shop drawing to be carried out by the specialist. Containment shall be sized such that a 25% spare capacity is available for any modifications to the system after handing over.

      - GROUNDING

        - Each piece of electronic equipment shall be properly grounded before energizing. All wire shields shall be grounded at the hub end only, not at the remote or device end. Grounding system components consists of conductor and cable shields to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

      - TESTING AND COMMISSIONING

        - All tests shall be carried out according to a detailed procedure duly approved by the engineer and as stated in section 26 01 26. The tests shall be carried out in phases.

        - Cables are to be tested for any damage occurred during transportation to site and/or during the course of pulling-in and laying.

        - Pre-testing: Upon completing installation of the system, align, adjust and balance the system and perform complete pre-testing. Determine, through the pre-testing, the conformance of the system to the requirements of the drawings and specifications. Correct deficiencies observed in pre-testing. Replace malfunctioning or damaged items with new and retest until satisfactory performance and conditions are achieved. Prepare forms for systematic recording of acceptance test results.

        - Report on Pre-testing: After pre-testing is complete, provide a letter certifying the installation is complete and fully operable, including the names and titles of the witness to the preliminary tests.

        - Final test notice: Provide a 10-day minimum notice in writing when the system is ready for final acceptance testing.

        - Resetting: Correct deficiencies indicated by tests and completely retest work affected by such deficiencies. Verify by the system test that the total system meets the specifications and complies with the applicable standards.

      - TRAINING

        - Engage a factory-authorized service representative, whose credentials are approved by the engineer, to explain programming and operation of system and to train Employer's maintenance personnel on procedures and schedules for maintaining, programming, operating, and adjusting, troubleshooting, and servicing system.

        - Training shall be carried out to an approved training manual Separate training shall be provided on the hardware and software. Each training shall have both class room session and hands on session. Contractor shall allow for 6 trainees each in both the trainings.

- END OF SECTION