- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Lighting and Power Panel boards including cabinet cut out boxes and enclosures.

      - REFERENCES

        - IEC 947		     LV Switchgear and Control gear.

        - BS EN 60439-3   LV Enclosures.

        - BS 5486:1989	     LV Switchgear.

        - BS EN 60947       Molded Case Circuit Breakers.

        - IEC 898                Miniature Circuit Breakers.

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

        - Provide samples of all proposed panels, devices, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

      - QUALITY ASSURANCE

        - Manufacturer’s: Firms regularly engaged in the manufacture of panel boards and enclosures of the types, sizes and ratings required, whose products have been in satisfactory use in similar service for not less than 10 years.  Preference shall be given to local manufacturers and agents/suppliers.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

        - Comply with the requirements of BS, IEC and Local Standards.

      - DELIVERY, STORAGE AND HANDLING

        - Handle Panel boards and enclosures carefully to prevent breakage, denting or scoring the finish. Store panel boards and enclosures at indoor location and protect from weather. When necessary to store outdoors, elevate well above ground and enclose with durable, waterproof wrapping and protect from direct sun.

      - SPARE PARTS

        - Supply as maintenance stock, additional circuit breakers, relays and fuses of the panel boards, amounting to one unit for every 10 units, but not less than 5 units of each type and rating.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - All materials specified herein shall be of high quality and of proven suitability for the functions they will perform and the conditions they will meet in service.

        - All panel boards, shall be of the same brand and of similar brand as that of LV Switchboards.

        - All circuit breakers shall be of the same brand.

      - PANELBOARD CONSTRUCTION

        - Lighting, power, branch circuit and distribution panel boards shall conform to BS EN 60529 , IEC 529 and BS EN 60439-3 requirements. The technical requirements showing bus size, size and number of branch circuit breakers, branch circuit loads and wiring as provided for each panel board in the Contract Documents shall be followed for guidance and panel boards shall be upgraded for actual site requirements before fabrication.

        - Panel boards, cabinet boxes and enclosures shall be suitable for recessed or surface mounting as required on site.

        - Interior components shall be mounted on back plate of reinforced steel for rigid support and accurate alignment.

        - One flat key tumbler cylinder type door lock with two keys per lock shall be provided.

        - Provide enclosure earthing in accordance with requirements given in Section 26 05 26.

        - Bus bars shall be hard drawn high conductivity copper, with silver plated contact surface.

        - Finish shall be baked gray enamel with rust inhibitor.

        - Provide circuit breakers in accordance with Section 26 28 23.  Provide two adjacent single pole breakers to opposing polarities in such a manner that two pole breakers can be installed in any location.  The same shall be provided for three adjacent single pole breakers to opposing polarities.

        - Where shown on panel’s schedule, panel boards shall be with split bus bars.

        - Neutral and ground bus bars shall be of the same rating as the phase bus bar.

        - A separate earthing bus bar, marked with a yellow green strip along its front and bonded to the steel cabinet, shall be provided for connecting all earth conductors. Bus bars shall be copper, shall be securely fastened to bases, and shall not depend upon breakers for support. All main buses and back pans shall be so designed that branch breakers may be changed without additional machining, drilling or tapping.

        - Panel board assemblies shall be so designed that any individual breaker can be removed without disturbing adjacent units or without loosening or removing supplemental insulation supplied as a means of obtaining clearances.

        - Provide panel board accessories and devices including, but not necessarily limited to, cartridge and plug time-delay type fuses, circuit breaker, earth fault protection units, etc., as recommended by panel board manufacturer for ratings and applications indicated.

        - One 25 mm wide laminated plastic name plate shall be attached by means of stainless steel rivets or permanent adhesive, showing panel board number in 13 mm white cut-in letters on black background.  All labeling and identification shall be in accordance with section          26 05 53.

        - A directory holder with clear plastic or glass plate and metal frame shall be mounted on the inside of each door.

        - Protection degree shall be a minimum of IP 31 for indoor and IP 54 for outdoor installations.

        - Construction shall allow maintenance of incoming line terminations, main device connections and all main bus bolted connections to be performed without rear access.

      - LIGHTING AND POWER PANELBOARDS

        - The lighting and power panel boards shall be of the dead front type with bolt-on circuit breakers in the mains, if indicated, and branches.  The panel boards shall be designed for 400/230 V as shown on the Drawings, 3-phase, 4-wire, 50 Hz application.

        - The lighting and power panel boards shall be equipped with bolt-on type circuit breakers.  Circuit breaker ratings shall be as shown in the panel board schedules.

        - Continuous current rating of bus bars shall be as shown on panel board schedules.

        - Where shown on panel’s schedule, panel boards shall be with split bus bars.

        - Where a main protective device is not shown, provide disconnect switches.  Bus bar and branch devices shall be of the sequence-phase type connections.

        - Neutral and grounding bars shall be mounted at the opposite end of the structure from the mains and with numbered terminals for connection of neutral and grounding wires.

        - Panel boards shall be provided with earth leakage protection devices as shown in panel board schedules, and in compliance and Local Electricity Authorities codes.

      - DISTRIBUTION PANELBOARDS

        - Distribution panel boards shall be of the dead front type and shall be designed for 400/230 V, 3-phase, 4-wire, 50 Hz applications.  Each distribution panel shall be enclosed in a sheet metal cabinet with front doors, catches, locks, etc.  Locks shall be fitted for the same key as locks on other lighting and power branch circuit panel boards.  All distribution panel boards shall meet pertinent standards.

        - The distribution panel boards shall be equipped with bolt-on molded case circuit breakers.  Circuit breaker ratings shall be as shown on the distribution board schedules.

        - Current-carrying connections to bus shall be of the bolted type, factory assembled.  Bus bars shall be of the sequence-phase type connections and arranged for 3-phase, 4-wire mains or lugs.

        - Mount the neutral bar at the opposite end of the structure from the mains and with have numbered terminals for connection of neutral wires.

        - Where shown on panel’s schedule, panel boards shall be with split bus bars.

        - Panel boards shall be provided with earth leakage protection devices as shown in panel board schedules, and in compliance Local Electricity Authorities codes.

      - NAME PLATES

        - Comply with Section 26 05 53.

        - Each panel board shall have an affixed engraved nameplate.  The nameplate shall be both in English and Arabic.

        - Each distribution panel board circuit breaker shall be equipped with a nameplate which indicates the name of the equipment (motor, panel board, etc.) to which the feeder conductors are connected.  Where more than one piece of equipment or panel board is connected to the circuit this fact shall be indicated on the nameplate. Apply the feeder numbers as shown on the Drawings on the switch nameplates.

- EXECUTION

      - INSTALLATION

        - Install panel boards, cabinet boxes and enclosures including electrical connections, in accordance with the manufacturer's written instructions, applicable requirements of Local Standards/ regulations, BS and IEC and in accordance with recognized industry practices to ensure that products serve the intended function.

        - Co-ordinate installation of panel boards and enclosures with cable and raceway installation work.

        - Install only in permanently dry locations, away from all mechanical and public health services.

        - Anchor enclosure firmly to walls and structural surfaces, ensuring that they are permanently mechanically secured.

        - Check ratings of all circuit protection devices and other components according to approved material.

        - Provide electrical connections within enclosures.

        - Fill out panel board's directory card upon completion of installation works.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - Prior to energization of circuiting, check all accessible connections to manufacturer's torque specifications.

        - Prior to energization of panel board, check with earth resistance tester phase-to-phase and phase-to earth insulation resistance levels to ensure requirements are fulfilled.

        - Prior to energization, check panel board for electrical continuity of circuits and for short circuits.

      - ADJUSTING

        - Subsequent to wire and cable hook-ups and testing, energize panel boards and demonstrate functioning in accordance with the requirements. Check whether all outgoings are connected as per panel board schedules.  Record changes in the schedules for final as-built, if acceptable to the Engineer.

- END OF SECTION