- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Cable trays.

          - Cable Ladders

        - Related Sections And Documents

          - Drawings and general provisions of the Contract, including General and Supplementary Conditions.

      - REFERENCES

        - BS EN ISO 1416.

      - SUBMITTALS

        - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

        - Shop Drawings: Indicate tray type, dimensions, support points, and finishes.

        - Product Data: Submit fittings and accessories.

        - Provide samples of all proposed cable trays, suspension rods, supports, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Provide method statement for installation, testing and commissioning of cable trays complete with loading calculations.

        - Manufacturer's Installation Instructions: Submit application conditions & limitations of use stipulated by Product testing agency specified under Regulatory Requirements. Include instructions for storage, handling, protection, examination, preparation, & installation of Product.

      - QUALIFICATIONS

        - Manufacturer: Company specializing in manufacturing Products specified in this section with minimum three years documented experience, and with service facilities within 100 miles of Project.

      - QUALITY ASSURANCE

        - Cable Trays shall comply with the applicable standards of Local Standards Organization & BS.

        - Building fabric shall be made good to the satisfaction of the Engineer.

        - Source Limitations: Obtain cable tray components through one source from a single Manufacturer.

      - DELIVERY, STORAGE AND HANDLING

        - All Cable Trays shall be delivered in factory pack wrapping and boxes and stored in a clean, dry space within the racks.

      - SPARE PARTS

        - Supply as maintenance stock, additional consumable material of all types and sizes used, per Supplier’s recommendations.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - CABLE TRAYS

        - All cable trays shall be of heavy-duty perforated type with return flange not less than 50 mm.

        - All cable trays shall be hot-dip zinc coated galvanized steel after manufacture according to BS EN ISO 1416, with a standard heavy-duty galvanizing coating of 350 g/m2 and Z2 bending grade.

        - Provided all manufacturer's standard accessories and fittings such as clamps, hangers, brackets, splice plates, reducer plates, blind ends, barrier strips, connectors, grounding straps and angles shall be of the same specification as that of the cable tray finish and shall be standard products from the same manufacturer as the cable tray. Site fabrication shall not be permitted.

        - Cable trays and accessories shall be of a thickness of not less than:

          - 1.5 mm up to 450 mm width.

          - 2 mm above 450 mm width.

        - All fixing brackets, nuts and bolts shall be finished by hot dip galvanizing.

        - Tinned copper earth continuity straps shall be provided at every joint of the cable tray.

        - Where cable tray crosses building expansion joints, the tray shall be installed suitably to provide expansion / contraction with the building expansion.

        - Where cable tray carries 11 kV cable, a tray lid shall be installed.

        - In outdoor locations and areas subject to corrosive atmospheres, all cable trays shall be painted with chlorinated rubber paint or PVC/Epoxy coating, as approved by the Engineer.

        - Outdoor cable trays installations shall be provided with flanged covers of the same material.

      - CABLE LADDERS

        - All cable ladders shall be heavy duty gauge (>2 mm), manufactured from hot-dip galvanized steel after manufacture according to BS EN ISO 1416 with a standard heavy-duty galvanizing coating of 350 g/m2 and Z2 bending grade.

        - All accessories and fittings such as couplers, bends, tees, elbows, etc. shall be by the same manufacturer as the ladder.

        - Ladder system supports shall be determined in accordance with the manufacturer's structural information to ensure that undue stress or bending shall not occur.

        - Tinned copper earth straps shall be provided at every joint of cable ladder.

        - In outdoor locations and areas subject to corrosive atmosphere, the ladders shall be painted with chlorinated rubber paint or PVC/Epoxy coating, as approved by the Engineer.

      - WARNING SIGNS

        - Engraved Nameplates: black letters on yellow laminated plastic nameplate, engraved with: WARNING! DO NOT USE CABLE TRAY AS WALKWAY, LADDER, OR SUPPORT? USE ONLY AS MECHANICAL SUPPORT FOR CABLES AND TUBING!

- EXECUTION

      - CABLE TRAY / CABLE LADDER INSTALLATION

        - Install as a complete system, including all necessary fasteners, hold-down clips, splice-plate support systems, barrier strips, hinged horizontal and vertical splice plates, elbows, reducers, tees, and crosses.

        - Remove burrs and sharp edges from cable trays / cable ladders.

        - Make connections to equipment with flanged fittings fastened to cable tray / cable ladder and to equipment. Support cable tray / cable ladder independent of fittings. Do not carry weight of cable tray / cable ladder on equipment enclosure.

        - Install expansion connectors where cable tray / cable ladder crosses building expansion joint. Space connectors and set gaps according to applicable standard.

        - Make changes in direction and elevation using standard fittings.

        - Make cable tray / cable ladder connections using standard fittings.

        - Sleeves for Future Cables: Install capped sleeves for future cables through firestop-sealed cable tray / cable ladder penetrations of fire and smoke barriers.

        - Workspace: Install cable trays / cable ladders with enough space to permit access for installing cables.

        - Install barriers to separate cables of different systems, such as power, communications, and data processing; or of different insulation levels, such as 600, 5000, and 15 000 V.

        - After installation of cable trays / cable ladders is completed, install warning signs in visible locations on or near cable trays / cable ladders.

      - CABLE INSTALLATION

        - Install cables only when cable tray / cable ladder installation has been completed and inspected.

        - Fasten cables on horizontal runs with cable clamps or cable ties. Tighten clamps only enough to secure the cable, without indenting the cable jacket. Install cable ties with a tool that includes an automatic pressure-limiting device.

        - On vertical runs, fasten cables to tray every 300 mm. Install intermediate supports when cable weight exceeds the load-carrying capacity of the tray rungs.

        - In existing construction, remove inactive or dead cables from cable tray / cable ladder.

        - Install covers after installation of cable is completed.

      - CONNECTIONS

        - Ground cable trays / cable ladders according to manufacturer's written instructions and as per regulations.

        - Install an insulated equipment grounding conductor with cable trays / cable ladder.

      - FIELD QUALITY CONTROL

        - After installing cable trays / cable ladders and after electrical circuitry has been energized, survey for compliance with requirements. Perform the following field quality-control survey:

          - Visually inspect cable insulation for damage. Correct sharp corners, protuberances in cable tray / cable ladder, vibration, and thermal expansion and contraction conditions, which may cause or have caused damage.

          - Verify that communication or data-processing circuits are separated from power circuits by barriers.

          - Verify that there is no intrusion of such items as pipe, hangers, or other equipment that could damage cables.

          - Remove deposits of dust, industrial process materials, trash of any description, and any blockage of tray ventilation.

          - Visually inspect each cable tray / cable ladder joint and each ground connection for mechanical continuity. Check bolted connections between sections for corrosion. Clean and re-torque in suspect areas.

          - Check for missing or damaged bolts, bolt heads, or nuts. When found, replace with specified hardware.

          - Perform visual and mechanical checks for adequacy of cable tray / cable ladder grounding; verify that all takeoff raceways are bonded to cable tray / cable ladder.

        - Report results in writing.

      - PROTECTION

        - Protect installed cable tray / cable ladders.

          - Repair damage to galvanized finishes shall be lead lined as recommended by cable tray / cable ladder manufacturer.

          - Install temporary protection for cables in open trays to protect exposed cables from falling objects or debris during construction. Temporary protection for cables and cable tray / cable ladder can be constructed of wood or metal materials until the risk of damage is over.

- END OF SECTION