SECTION 21 30 00

FIRE PUMPS

PART 1 GENERAL

- SUMMARY

- Section Includes:

- Fire pumps.

- Fire pump accessories.

- Electric motor drive.

- Pressure booster (jockey) pump.

- PERFORMANCE REQUIREMENTS

- All pumps, drivers and controllers components shall conform to NFPA 20 2010 edition, if a contradiction between this specification and NFPA 20 is found the requirement that best serves the performance of the equipment shall be followed.

- SUBMITTALS

- Shop Drawings: Required.

- Product Data: Required, manufacturers printed and fill attached data sheet.

- Field Test Reports: Required.

- Manufacturer's Installation Instructions: Required.

- Manufacturer's Certificate: Required.

- Compliance sheet with: This specification and NFPA 20.

- CLOSEOUT SUBMITTALS

- Project Record Documents: Required.

- Operation and Maintenance Data: Required.

- QUALITY ASSURANCE

- Perform Work in accordance with UL Fire Protection Equipment Directory.

- WARRANTY

A. 	Furnish five year manufacturer warranty for fire pumps.

- MAINTENANCE SERVICE

A. 	Furnish service and maintenance of fire pump, driver, and controller for two years from Date of Substantial Completion.

PART 2 PRODUCTS

- FIRE PUMPS

- Type: vertical turbine type, UL 448 and FM 1311, direct connected for 17.2 bar maximum working pressure.

- Casing: Cast Iron having a minimum tensile strength of 35,000 PSI, with suction and discharge gage port, casing replaceable bronze wear ring, seal flush connection, drain plug, flanged suction and discharge. Bearing housing supports, and suction and discharge flanges shall be integrally cast with the lower half of the casing. Removal of the upper half of the casing must allow the rotating element to be removed without disconnecting the suction and discharge flanges.

- Bearings: Grease lubricated ball bearings, replaceable without opening casing.

- Impeller: Bronze double suction fully enclosed, statically and dynamically balanced and keyed to shaft.

- Shaft: Stainless steel with replaceable brass sleeve through seal chamber.

- Seal: Packing gland with minimum four rings graphite impregnated packing and bronze lantern rings, 110 degrees C maximum continuous operating temperature.

- Drive: Flexible coupling with coupling guard.

- Mounting Feet: The mounting feet of the pump shall be machined perpendicular to the shaft. The pump shall be bolted to an extra heavy cast iron drip rim ring base. The top of the pump shall be machined to receive the motor mounting bracket. The mounting bracket shall be machined with registered fits to align pump and motor.

- Performance: Pumps shall furnish not less than 150 percent of rated capacity at not less than 65 percent of total rated head. The shutoff head shall not exceed 140 percent of rated head.

- Pump shall be painted red by the manufacturer.

- FIRE PUMP ACCESSORIES

- Eccentric suction reducer and OS&Y gate valve on suction side of pump.

- Concentric increaser and check valve in pump discharge and indicating butterfly valve on system side of check valve.

- For diesel engine driven pumps only; main relief-valve, UL 1478 and FM 1361, and open type waste cone.

- Suction pressure gage, 110 mm diameter dial with snubber, valve cock and lever handle.

- Discharge pressure gage mounted on board attached to pump, with snubber, valve cock and lever handle.

- Casing relief valve, not less than 20mm.

- Float operated automatic air release valve, not less than 20mm.

- Flow metering system for closed loop testing. FM Approved Venturi Type Metering device, shall be capable of handling water flow of not less than 175% of rated pump capacity.

- Flexible drive coupling, with OSHA approved guard.

- Pressure sensing line.

- Ball drip valve: UL 1726

- One manufactures nameplate for pump, stating:

- Pump capacity

- Total head

- Pump RPM

- Manufacturer’s	model and serial number

- Casing working pressure

ELECTRIC MOTOR DRIVE

Motor: Squirrel cage induction type; in totally enclosed NEMA MG-1 enclosure, 2950 rpm with name plate. The motor shall be of such capacity that 115% of the full-load ampere rating shall not be exceeded at any condition of pump load. Locked rotor current shall not exceed the values specified in NFPA 20.

2.3

- Controller: Microprocessor Electric Controllers service type with wye-delta starter in NEMA Type 4 drip proof enclosure, including the following:

- Disconnect Switch: Externally operable, quick break type.

- Circuit Breaker: Size to NFPA 20, minimum 65,000 amperes interrupting capacity.

- Motor Starter: Energized automatically through pressure switch or manually by externally operable handle.

- Pressure Switch: To withstand 400 psi, Set to cut in at 10.8 bar, value must be confirmed on site..

- Pressure recording device: To withstand 400 psi.

- Running Period Timer: Keeps motor in operation when started automatically, for minimum of seven minutes.

- Pilot Lamp: Indicates circuit breaker closed and power available.

- Phase reversal indicator.

- Pump or motor running signal to fire alarm panel.

- Loss of phase alarm for both running and rest modes.

- Test Accessories: Ammeter test link and voltmeter test studs.

- Alarm Relay: Energizes alarm to indicate circuit breaker open or power failure.

- Switch Relay: For remote start.

- Manual Selector Station: On enclosure marked "Automatic" and "Non-Automatic."

- Locked Rotor Over current Protection.

- Signals should be remotely monitored in accordance with NFPA 20.

- Fire Pump Controller and Transfer Switch combination

- The Fire Pump Controller and Transfer Switch combination shall meet the requirements of the latest edition of NFPA 20 and shall be UL listed for the use with fire pump sets

- The transfer switch shall meet UL 1008 and shall be regularly subjected to Endurance, Interrupting Capacity, and Dielectric Voltage-Withstand test as outlined by UL 489 standards.

- The transfer switch shall be suitable for the available short circuit current at the line terminals of the controller

- The contractor shall determine the proper current rating of the transfer switch as per the final and approved selection of the fire pump noting that the ampere rating shall not be less than 115% of the motor full-load current.

- The transfer switch shall be installed in a barriered compartment of the fire pump controller. The complete assembly, controller and transfer switch, shall be shipped as a single unit.

- A single uni-gear motor shall electrically operate the transfer mechanism. It shall also be capable of being operated manually and shall have suitable provisions for readily disengaging the gear motor when necessary.

- The transfer switch shall be mechanically and electrically interlocked so that it shall not be possible for the load circuits to be connected to normal and emergency sources simultaneously, regardless of whether the switch is electrically or mechanically operated. The switch shall have a manual neutral.

- The alternate side shall be provided with an isolation switch sized to a minimum of 115% of the motor fullload current and a circuit breaker having a continuous current rating not less than 115% of the motor full load amps. The isolation switch shall have overcurrent sensing elements of the non-thermal type, and instantaneous short-circuit overcurrent protection. (This does not apply to FPATS Stand Alone and FT20 Limited Service Transfer Switch Controllers.)

- The isolating switch and circuit breaker shall be mechanically interlocked and operated by a single handle.

- An auxiliary contact shall be provided to prevent sending of the signal for starting of the alternate source generator when the transfer switch commands it, if the isolation switch on the alternate source side of the transfer switch is open.

- The transfer switch shall be provided with locked rotor overcurrent protection. The locked rotor protector shall be calibrated and set to a minimum of 300% of the motor full-load current and have a tripping time between 8 and 20 seconds.

- A solid state sensing and control logic panel shall be separately mounted from the power-switching portion of the transfer switch. The two sections shall be connected together by control cables and plug-in connectors. The control section shall be capable of being isolated from the power section for maintenance.

- The normal power source shall be set to pickup at 95% and drop out at 85% of nominal supply. The voltage sensing on the alternate supply shall be set to pickup at 95% of nominal voltage.

- All voltage sensing, frequency sensing, and timer set points shall be field adjustable.

- The transfer switch shall automatically transfer its load circuit to an emergency or alternate power supply upon failure of the normal or original supply. In order to override momentary fluctuations in the system, a time delay transfer from normal to alternate power supply shall be adjustable up to 1800 seconds. Upon restoration of the normal supply, the transfer switch shall automatically retransfer its load circuits to the normal supply. Mechanically held transfer mechanisms shall be energized only momentarily during transfer or retransfer.

- If the emergency / standby power should fail while carrying the load, transfer to the normal supply shall be made instantaneously upon restoration of the normal source to satisfactory conditions.

- The transfer switch shall come complete with five LED's to provide visual indication of the unit status, source 1 available, source 1 connected, source 2 available, and source 2 connected.

- An engine test button shall be provided that will initiate an engine test.

- A silence alarm button shall be provided that will silence the alarm buzzer.

- 1 No. of Form-C contact shall be provided for remote indication for source 1 connected or source 2 connected

- 2 No. of Form-C contacts shall be provided for remote indication for the alternate source-isolating switch open.

- PRESSURE MAINTENANCE (JOCKEY) PUMP

- Electrically operated vertical multistage inline type with standard open drip-proof motor.

- Control by automatic jockey pump controller with full voltage starter, and minimum run timer, to start pump on pressure drop in system and stay in operation for minimum period of time. Fire pump starts automatically on further pressure drop or on jockey pump failure. Controller shall have power failure alarm, phase reversal alarm, Pump running signal.

- Jockey pump shall have:

- Horsepower rated disconnect switch, fuse block and fuses.

- Horsepower rated motor contactor and overload relay.

- Minimum run timer to prevent short cycling of pump.

- HAND-OFF-AUTO selector switch to allow manual operation of the pump.

- Pressure Switch to withstand 400 psi.

- SEQUENCE OF OPERATION

- Fire Water Pumps shall be configured to start automatically upon a confirmed fire condition and shall be implemented in accordance with the requirements of NFPA 20. The fire pump controller shall initiate automatic starting of the duty fire pump upon sensing loss of pressure in the Fire Water Distribution System.

- Should the duty electric fire water pump fail to start or is unable to restore pressure in the Fire Water Distribution system then the standby fire water pump shall start within a set time interval (nominally 10 seconds) Failure of any one pump to start shall not prevent subsequent starting of the other pump.

PART 3 EXECUTION

- INSTALLATION

- Install Fire Pump in accordance with NFPA 20 .

- Install piping for fuel supply and return. Connect to motor. Install piping to and from exhaust silencer with thimble at wall or roof penetrations.

- Perform flow test on entire system in accordance with NFPA 20.

- Schedule test in accordance with NFPA 20 to be witnessed by required parties.

- Demonstration and Training: Demonstrate automatic operation of system including verification of pressure switch set points. Including training to Owner.

- Piping: All piping shall be constructed from ASTM A105 or ASTM A53 standard weight pipe. The package piping shall consist of fabricated welded steel and / or cast iron in and out of the pumps. All piping shall be sized per NFPA 20. All welded pressure bearing piping must be fabricated with full penetration welds. Use of backing rings will not be permitted. Qualification of the welding procedures and performance of the welders shall comply with the requirements of ASME code, Section IX. All frame welds shall be performed by ASME qualified welders per Section IX of the ASME Code. After fabrication and before coating piping shall be blasted inside and out to SSPC SP 10, near white metal and hot dip galvanized. All piping, valves and fittings shall be in accordance with NFPA 20. Supports shall be provided for all suction and discharge piping. All pipe supports shall be designed to allow for the removal of any individual sections without adding additional stress to adjoining sections.

- Painting: After fabrication and before shipping paint all surfaces including but not limited to the main piping and structural members, excluding the fuel lines, enclosure fire sprinkler lines and jockey pump piping as follows:

Moderate Exposure Surface Preparation - SSPC-SP10 abrasive blasting to a near white metal finish resulting in a 1.5 to 2.5 mil surface profile. First Coat Polyester Urethane applied at 3-5 MDFT directly to prepared substrate.

END OF SECTION