SECTION 23 8128

DX SPLIT AIR CONDITIONING UNITS & VRF System

General

- The air conditioning system employed in the project shall be Variable Refrigerant Flow/ Variable Refrigerant Volume (VRF/VRV) utilizing refrigerant R410a.

- The system will provide either a heating or cooling operation to all indoor units. An electronic injection valve controlled by the Micro-processor system controller provides an optimum level of fill for the evaporator, overheating, and the defrost cycle.

- Manufacturers:  regularly engaged in the manufacture of VRF air conditioning system whose VRF products have been in satisfactory use in similar service in Jordan for not less than 10 years.

- Supplier: Firms in Jordan regularly engaged in servicing and installing VRF air conditioning equipment of a similar quality and scope as this project for at least 5 years.

- Supplier has to present a warranty based on unit’s country of origin (parts & assembly) as the following :

- Japan, Europe, USA, Korean, & Local: 3 years from date of commissioning.

- Other origins:

- 7 years from date of commissioning.

- The Contractor shall provide to the end user 3 years maintenance warrantee from Defect Notification Period inclusive of parts and workmanship free of charge for the other origins mentioned above.

- Supplier has present official certificate from the manufacture to confirm the availability of spare parts for 15 years.

- Brand name shall be Eurovent certified. COP shall be not less than 3.5 and EER shall be not less than 3.0 for all outdoor units according to Eurovent certification.

Submittals

- The Supplier must have official certificated Experience in installing & servicing a several types of projects with large capacities of the same selected brand name in Jordan.

The submitted air conditioning units shall be installed in projects in Jordan for more than 5 years, and it is still working with good performance. The supplier shall provide recommended spare parts (list & prices) for the system can cover 5 years from commissioning date.

- The selected brand shall be of the most known & famous top quality types which meet or exceed specified requirements. The supplier must provide certificate of origin for assembly and main parts such as - not limited to -compressor, condenser fans, motors, microprocessor controller,

- inverters and any other parts subject to engineer request. The certificates of Origin shall be approved by Ministry of Industry & Trade of Jordan.

- The submittal shall show all technical data such as not limited to – total and sensible capacities, air flow rate, off coil temperatures and any other values subject to engineer request.

- The supplier shall specify the manufacturer name and all the technical data for the main components such as - not limited to -compressor, condenser fans, motors, microprocessor controller, inverters and any other parts subject to request.

Outdoor Unit

- Outdoor module shall include scroll or rotary compressor.

- The inverter of the compressor must be general drive programmable, can operate any BLDC compressor in case of future failure.

- The inverter of the compressor must be general drive programmable, can operate any BLDC compressor in case of future failure.

- The inverter compressors modulate output to meet the exact demand of the indoor units. Outdoor units shall be energy saving units. The selected proposed system shall have (based on the actual required capacities including the actual pipe total length & the actual level difference between indoor and outdoor units (including all piping losses)) low power consumption and low running currents.

- Outdoor unit shall be light weight, vibration free with high-capacity (the lighter units are preferred).

- Condenser /evaporator optimized for 410A refrigerant.

- The condensing unit must be designed with separate air flow and mechanical compartments with high protection of mechanical and electronic

- Compartments in extreme weather conditions. Service maintenance shall be easy with simple access to serviceable parts.

- Outdoor  Modules shall be full inverter

- For back up operation:

- In case of inverter compressor failure in one module, the outdoor keeps operating with the remaining compressors in the other modules.

- Compressors operation management: as the load increases all the compressors in outdoor unit shall have an individual equal working time.

- DIGITAL Compressors are not allowed.

- Control sensors shall be provided for low pressure, high pressure, refrigerant suction temperature, oil temperature, heat exchanger temperature and outside temperature.

- Safety pressure switches shall be provided for low and high pressure, and differential pressure switch shall be provided for block coil. The unit shall be equipped with shut-off valves for suction and liquid pipes and service connections.

- Outdoor unit’s condenser must be with maximum 12 fins / inch for maintenance and cleaning issues, post coating for tubes & fins shall be provided for corrosion resistance

- Condenser fans shall have Aluminum or Iron plates, other materials are subject to engineer approval, Fans motors shall be DC type.

- (100% combination).

- Operating temperature range:

- Heating: -20°C DB to 18°C WB.

- Cooling: -5°C DB 48.0°C DB.

- The Outdoor Units must be Selected based on the following conditions :

- Heating: 0°C DB Outside, 22°C DB Inside.

- Cooling: 38°C DB Outside, 23°C DB/16°C WB Inside room temperature.

- On coil & off coil shall be based on cooling load schedules.

Refrigerant Piping

- Furnish complete Pipe network with all accessories and specialties between indoor /AHUS & outdoor units

- Piping Limitations:

- Allowable total length: 	1000 meters

- Furthest Indoor Unit: 		150 meters

- Height difference between indoor and outdoor units: 50 meters

- Copper pipes specifications: MULLER type l nitrogenized acr/med or equivalent. All brazed joints shall be accessible for future inspection & leak detection (provide access doors)

- Furnish thermal insulation for refrigerant piping of minimum 13 mm closed cell elastomeric rubber (the insulation must be covered with Insulation Tape for indoor pipes and for exposed pipes to add 3Layers of Cora cloth with water base Foster adhesive) and all external pipes shall be cladded with Aluzinc.

- Pipes shall be hanged on ceiling & walls by rubber lined split pipe clamps (Tightening scope , MS rods & anchors M8 min. Pipes shall be supported on roof by rubber lined split pipe clamps (Tightening scope) , MS rods & anchors M10 min. mounted on concrete block bases .

Master Microprocessor Controller

- Furnish microprocessor controller to perform the following functions: control & regulating of cooling & heating cycles, Management function of all sensors and actuators, control of all safety devices, Oil balance between compressors, automatic management of all indoor units on the system  bus, low noise night operation, Duty, standby & hours management of compressor, & self-diagnosis functions of outdoor & indoor. The controller must be native BACnet communicator.

- The controller shall offer control, monitoring, scheduling, service & maintenance functions for outdoor unit & indoor units in the building individually or as groups.

- The controller can provide the following as options:

- Function ON/OFF state

- Mode of operation

- Room temperature

- Set temperature

- Fan speed

- Filter reset & sign

- Service & maintenance functions

- Controlling the ventilation system

- Energy consumption calculation

- Emergency stop

- All above functions are subject to engineer request and must be decided before, based on projects requirement.

- MMC shall introducing full colored extended touch screen.

- In case of MMC can’t achieve the above required functions, centralized controller shall be provided.

Indoor Units

- Indoor units shall be cassette, wall mounted with outside decorative cover or ceiling types.

- The Indoor Units must be selected based on the total, sensible capacities and required off coil temperatures at actual on coil temperatures, and air flow rate at actual external static pressure.

- The height of indoor units is important factor: slim units are recommended.

- The height of indoor units for normal Cassette type must not exceed 300 mm.

- The thermostat of indoor units must be fixed in wall, except the wall mounted units which shall have remote control.

- Ducted Units shall have 0.5 – inch fiber glass insulation, and shall be provided with Aluminum type long life washable filter.

- Ducted units fan motors shall be UL-Certified.

- Auto Restart: Built in auto restart capability to ensure automatic system start after power failure and it should be activated or deactivated based on client requirement.

- The coil shall be made of HI-X Cu piping with profiled Aluminum fins. The indoor unit shall be provided with electronic expansion valve for precise refrigerant adjustment 0%-100%.

- The outdoor & indoor units shall have serial communication which can provide operation mood for any number of indoors in case of maintenance for other units.

- The system shall operate even if there is only one single indoor unit run and for long time or if there is any electrical failure on the other units in the system, the supplier shall guarantee the

- outdoor unit’s compressors in such cases.

- Shut off service valves with charging port for both units’ pipes shall be installed on the indoor units, and where it’s required to protect the system in case of maintenance & electric power failure.

| Compliance Sheet |  |  |  |
| --- | --- | --- | --- |
| VRF |  |  |  |
| Ref. | General | Comply | Note |
|  | - The air conditioning system employed in the project shall be Variable Refrigerant Flow/ Variable Refrigerant Volume (VRF/VRV) utilizing refrigerant R410a. |  |  |
|  | - The system will provide either a heating or cooling operation to all indoor units. An electronic injection valve controlled by the Micro-processor system controller provides an optimum level of fill for the evaporator, overheating, and the defrost cycle. |  |  |
|  | - Manufacturers: regularly engaged in the manufacture of VRF air conditioning system whose VRF products have been in satisfactory use in similar service in Jordan for not less than 10 years. |  |  |
|  | - Supplier: Firms in Jordan regularly engaged in servicing and installing VRF air conditioning equipment of a similar quality and scope as this project for at least 5 years. |  |  |
|  | - Supplier has to present a warranty based on unit’s country of origin (parts & assembly) as the following : |  |  |
|  | - Japan, Europe, USA & Local: 3 years from date of commissioning |  |  |
|  | - Other origins: 7 years from date of commissioning |  |  |
|  | - Supplier has present official certificate from the manufacture to confirm the availability of spare parts for 15 years. |  |  |
|  | Submittals |  |  |
|  | - The Supplier must have official certificated Experience in installing & servicing a several types of projects with large capacities of the same selected brand name in Jordan. |  |  |
|  | - The submitted air conditioning units shall be installed in projects in Jordan for more than 5 years, and it is still working with good performance. The supplier shall provide recommended spare parts (list & prices) for the system can cover 5 years from commissioning date. |  |  |
|  | - The selected brand shall be of the most known & famous top quality types which meet or exceed specified requirements. The supplier must provide certificate of origin for assembly and main parts such as - not limited to -compressor, condenser fans, motors, microprocessor controller, inverters and any other parts subject to engineer request. The certificates of Origin shall be approved by Ministry of Industry & Trade of Jordan. |  |  |
|  | - The submittal shall show all technical data such as not limited to – total and sensible capacities, air flow rate, off coil temperatures and any other values subject to engineer request. |  |  |
|  | - The supplier shall specify the manufacturer name and all the technical data for the main components such as - not limited to -compressor, condenser fans, motors, microprocessor controller, inverters and any other parts subject to request. |  |  |
|  | Outdoor Unit |  |  |
|  | - Outdoor module shall has scroll or twin rotary DC inverter type compressor. |  |  |
|  | - The inverter of the compressor must be general drive programmable, can operate any BLDC compressor in case of future failure. |  |  |
|  | - The inverter compressor modulate output to meet the exact demand of the indoor units. Outdoor units shall be energy saving units. The selected proposed system shall have (based on the actual required capacities including the actual pipe total length & the actual level difference between indoor and outdoor units (including all piping losses)) low power consumption and low running currents, the cop shall be calculated based on the above actual power consumption and actual conditions & actual capacities must not be less than 3.5. |  |  |
|  | - Outdoor unit shall be light weight, vibration free with high-capacity (the lighter units are preferred). |  |  |
|  | - Condenser /evaporator optimized for 410A refrigerant. |  |  |
|  | - The condensing unit must be designed with separate air flow and mechanical compartments with high protection of mechanical and electronic compartments in extreme weather conditions. Service maintenance shall be easy with simple access to serviceable parts. |  |  |
|  | - Outdoor Modules shall be full inverter |  |  |
|  | - For back up operation: |  |  |
|  | - In case of inverter compressor failure in one module, the outdoor keeps operating with the remaining compressors in the other modules. |  |  |
|  | - Compressors operation management: as the load increases all the compressors in outdoor unit shall have an individual equal working time. |  |  |
|  | - DIGITAL Compressors are not allowed. |  |  |
|  | - Control sensors shall be provided for low pressure, high pressure, refrigerant suction temperature, oil temperature, heat exchanger temperature and outside temperature. |  |  |
|  | - Safety pressure switches shall be provided for low and high pressure, and differential pressure switch shall be provided for block coil. The unit shall be equipped with shut-off valves for suction and liquid pipes and service connections. |  |  |
|  | - Outdoor unit’s condenser must be with maximum 12 fins / inch for maintenance and cleaning issues, post coating for tubes & fins shall be provided for corrosion resistance. |  |  |
|  | - Condenser fans shall have Aluminum or Iron plates, other materials are subject to engineer approval, Fans motors shall be DC type. |  |  |
|  | - (100% combination). |  |  |
|  | - Operating temperature range: |  |  |
|  | - Operating temperature range: - Heating: -20°C DB to 18°C WB. |  |  |
|  | - Cooling: -5°C DB 48.0°C DB. |  |  |
|  | - The Outdoor Units must be Selected based on the following conditions : |  |  |
|  | - Heating: 0°C DB Outside, 22°C DB Inside. |  |  |
|  | - Cooling: 38°C DB Outside, 23°C DB/16°C WB Inside room temperature. |  |  |
|  | - On coil & off coil shall be based on cooling load schedules. |  |  |
|  | Refrigerant Piping |  |  |
|  | - Furnish complete Pipe network with all accessories and specialties between indoor /AHUS & outdoor units |  |  |
|  | - Piping Limitations: |  |  |
|  | - Allowable total length: 1000 meters |  |  |
|  | - Furthest Indoor Unit: 150 meters |  |  |
|  | - Height difference between indoor and outdoor units: 50 meters |  |  |
|  | - Copper pipes specifications: MULLER type l nitrogenized acr/med or equivalents. All brazed joints shall be accessible for future inspection & leak detection(provide access doors) |  |  |
|  | - Furnish thermal insulation for refrigerant piping of minimum 13 mm closed cell elastomeric rubber (for exposed pipes the insulation must be covered with 3Layers of Cora cloth with water base Foster adhesive ).All exposed pipes shall be cladded with Aluzinc. |  |  |
|  | - Pipes shall be hanged on ceiling & walls by rubber lined split pipe clamps (Tightening scope , MS rods & anchors M8 min. Pipes shall be supported on roof by rubber lined split pipe clamps (Tightening scope) , MS rods & anchors M10 min. mounted on concrete block bases . |  |  |
|  | Master Microprocessor Controller |  |  |
|  | - Furnish microprocessor controller to perform the following functions: control & regulating of cooling & heating cycles, Management function of all sensors and actuators, control of all safety devices, Oil balance between compressors, automatic management of all indoor units on the system bus, low noise night operation, Duty, standby & hours management of compressor, & self-diagnosis functions of outdoor & indoor. The controller must be native BACnet communicator. |  |  |
|  | - The controller shall offer control, monitoring, scheduling, service & maintenance functions for outdoor unit & indoor units in the building individually or as groups. |  |  |
|  | - The controller can provide the following as options: |  |  |
|  | - Function ON/OFF state |  |  |
|  | - Mode of operation |  |  |
|  | - Room temperature |  |  |
|  | - Set temperature |  |  |
|  | - Fan speed |  |  |
|  | - Filter reset & sign |  |  |
|  | - Service & maintenance functions |  |  |
|  | - Controlling the ventilation system |  |  |
|  | - Energy consumption calculation |  |  |
|  | - Emergency stop |  |  |
|  | - All above functions are subject to engineer request and must be decided before, based on projects requirement. |  |  |
|  | - MMC shall introducing full colored extended touch screen. |  |  |
|  | - In case of MMC can’t achieve the above required functions, centralized controller shall be provided. |  |  |
|  | Indoor Units |  |  |
|  | - Indoor units shall be cassette, wall mounted with outside decorative cover or ceiling types. |  |  |
|  | - The Indoor Units must be selected based on the total, sensible capacities and required off coil temperatures at actual on coil temperatures, and air flow rate at actual external static pressure. |  |  |
|  | - The height of indoor units is important factor: slim units are recommended. |  |  |
|  | - The height of indoor units for normal Cassette type must not exceed 300 mm. |  |  |
|  | - The thermostat of indoor units must be fixed in wall, except the wall mounted units which shall have remote control. |  |  |
|  | - Ducted Units shall have 0.5 – inch fiber glass insulation, and shall be provided with Aluminum type long life washable filter. |  |  |
|  | - Ducted units drain pan shall be stainless steel with 1.2 mm thickness. |  |  |
|  | - Ducted units fan motors shall be UL-Certified. |  |  |
|  | - Auto Restart: Built in auto restart capability to ensure automatic system start after power failure. |  |  |
|  | - The coil shall be made of HI-X Cu piping with profiled Aluminum fins. The indoor unit shall be provided with electronic expansion valve for precise refrigerant adjustment 0%-100%. Refrigerant adjustment 0%-100%. |  |  |
|  | - The outdoor & indoor units shall have serial communication which can provide operation mood for any number of indoors in case of maintenance for other units. |  |  |
|  | - The system shall operate even if there is only one single indoor unit run and for long time or if there is any electrical failure on the other units in the system, the supplier shall guarantee the outdoor unit’s compressors in such cases. |  |  |
|  | - Solenoid valves shall be installed on the indoor units, and shall be connected with dedicated switch to protect the system in case of maintenance & electric power failure. |  |  |
| End Of Section |  |  |  |