SECTION 21 1100

FACILITY FIRE-SUPPRESSION WATER-SERVICE PIPING

PART 1 GENERAL

- SECTION INCLUDES

- Water pipe.

- Valves.

- Fire Department connections.

- RELATED REQUIREMENTS

- Section 03 3000 - Cast-in-Place Concrete. (CSI)

- Section 05 5000 - Metal Fabrications. (CSI)

- Section 09 9113 - Exterior Painting. (CSI)

- Section 09 9123 - Interior Painting. (CSI)

- Section 21 0500 - Common Work Results for Fire Suppression.

- Section 21 1300 - Fire Suppression Sprinklers.

- REFERENCE STANDARDS

- ASME B16.3 - Malleable Iron Threaded Fittings: Classes 150 and 300; 2011.

- ASME B16.4 - Gray Iron Threaded Fittings Classes 125 and 250; 2011.

- ASME BPVC-IX - Boiler and Pressure Vessel Code, Section IX - Welding, Brazing, and Fusing Qualifications; 2015.

- ASTM A48/A48M - Standard Specification for Gray Iron Castings; 2003 (Reapproved 2012).

- ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless; 2012.

- ASTM A126 - Standard Specification for Gray Iron Castings for Valves, Flanges, and Pipe Fittings; 2004 (Reapproved 2014).

- ASTM A135/A135M - Standard Specification for Electric-Resistance-Welded Steel Pipe; 2009 (Reapproved 2014).

- ASTM A536 - Standard Specification for Ductile Iron Castings; 1984 (Reapproved 2014).

- ASTM A674 - Standard Practice for Polyethylene Encasement for Ductile Iron Pipe for Water or Other Liquids; 2010 (Reapproved 2014).

- ASTM A795/A795M - Standard Specification for Black and Hot-Dipped Zinc-Coated (Galvanized) Welded and Seamless Steel Pipe for Fire Protection Use; 2013.

- ASTM B61 - Standard Specification for Steam or Valve Bronze Castings; 2008 (Reapproved 2013).

- ASTM B63 - Standard Test Method for Resistivity of Metallically Conducting Resistance and Contact Materials; 2007 (Reapproved 2013).

- ASTM B584 - Standard Specification for Copper Alloy Sand Castings for General Applications.

- ASTM C94/C94M - Standard Specification for Ready-Mixed Concrete; 2015.

- ASTM D2657 - Standard Practice for Heat Fusion Joining of Polyolefin Pipe and Fittings;

2007.

- ASTM D3035 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Controlled Outside Diameter; 2015.

- AWWA C105/A21.5 - Polyethylene Encasement for Ductile-Iron Pipe Systems; 2010 (ANSI/AWWA C105/A21.5).

- AWWA C110/A21.10 - Ductile-Iron and Gray-Iron Fittings; 2012 (ANSI/AWWA C110/A21.0).

- AWWA C203 - Coal-Tar Protective Coatings and Linings for Steel Water Pipelines - Enamel and Tape-Hot-Applied; 2008 (ANSI/AWWA C203).

- AWWA C205 - Cement-Mortar Protective Lining and Coating for Steel Water Pipe, 4 in. (100 mm) and Larger - Shop Applied; 2012 (ANSI/AWWA C205).

- AWWA C206 - Field Welding of Steel Water Pipe; 2011 (ANSI/AWWA C206).

- AWWA C209 - Cold-Applied Tape Coatings for Steel Water Pipe, Special Sections, Connections, and Fittings; 2013 (ANSI/AWWA C209).

- AWWA C503 - Wet-Barrel Fire Hydrants; 2014 (ANSI/AWWA C503).

- AWWA C509 - Resilient-Seated Gate Valves for Water Supply Service; 2009 (ANSI/AWWA C509/C509a).

- AWWA C515 - Reduced-Wall, Resilient-Seated Gate Valves for Water Supply Service; 2015.

- AWWA C550 - Protective Interior Coatings for Valves and Hydrants; 2013.

AA.	AWWA C600 - Installation of Ductile-Iron Water Mains and Their Appurtenances; 2010 (ANSI/AWWA C600).

AB.	AWWA C901 - Polyethylene (PE) Pressure Pipe and Tubing, 1/2 In. (13 mm) Through 3 In.

(76 mm), for Water Service; 2008 (ANSI/AWWA C901).

AC.	AWWA M11 - Steel Water Pipe - A Guide For Design and Installation; 2004 w/Errata.

AD.	FM (AG) - FM Approval Guide; current edition.

AE.	NFPA 13 - Standard for the Installation of Sprinkler Systems; 2016.

AF.	NSF 372 - Drinking Water System Components - Lead Content; 2011.

AG.	UL (DIR) - Online Certifications Directory; current listings at database.ul.com.

- ADMINISTRATIVE REQUIREMENTS

- Coordination: Coordinate the installation of equipment and materials with size, location and installation of service utilities.

- Pre installation Meeting: Conduct a pre installation meeting at least one week prior to the start of the work of this section; require attendance by all affected installers.

- Sequencing: Ensure that utility connections are achieved in an orderly and expeditious manner.

- SUBMITTALS

- Welders Certificate: Include welders certification of compliance with ASME BPVC-IX.

- Product Data:

- Include data on pipe materials, pipe fittings, valves, and accessories.

- Provide manufacturer's catalog information.

- Indicate valve data and ratings.

- Show grooved joint couplings, fittings, valves, and specialties on drawings and product submittals, specifically identified with the manufacturer's style or series designation.

- Manufacturer's Certificate: Certify that products meet or exceed specified requirements.

- Samples: Submit two paper chip samples, length by width in mm (or	by inch) in size

illustrating range of colors and textures available for each surface finishing product scheduled.

- Test Reports: Factory certified tests to verify that short-term rupture strength for RTRP I (filament bound) jointing is 10.3 MPA (1,500 psi) or greater.

- Field Quality Control Submittals: Testing activities.

- Project Record Documents:

- Record actual locations of piping mains, valves, connections, fire hydrants, free-standing fire department connections, underground manholes and vaults, valve boxes, thrust restraints, and invert elevations.

- Identify and describe unexpected variations to subsoil conditions or discovery of uncharted utilities.

- Maintenance Data: Include installation instructions, spare parts lists, and exploded assembly views.

- Maintenance Materials: Furnish the following for Employer/Owner's use in maintenance of project.

- Valve Repacking Kits: One for each type and size of valve.

- QUALITY ASSURANCE

- Maintain at the project site a copy of each referenced document that prescribes execution requirements.

- Manufacturer Qualifications: Company specializing in manufacturing the products specified in this section with minimum ten years documented experience.

- Installer Qualifications: Company specializing in performing work of the type specified and with at least five years documented experience.

- Provide grooved joint couplings, fittings, valves, specialties, and grooving tools from a single manufacturer.

- Date stamp castings used for coupling housings, fittings, and valve bodies for quality assurance and traceability.

- Coupling Manufacturer:

- Perform on-site training by factory-trained representative to Contractor's field personnel in the proper use of grooving tools and installation of grooved joint products.

- Periodic job site visits by factory-trained representative to ensure best practices in grooved joint installation.

- A distributor's representative is not considered qualified to perform the training.

- Welder Qualifications:

- Certify in accordance with ASME BPVC-IX.

- Provide certificate of compliance from local Authority Having Jurisdiction, indicating approval of welders.

- Valves: Bearing product listing label or marking. Provide manufacturer's name and pressure rating marked on valve body.

- Products:

- Listed, classified, and labeled as suitable for the purpose specified and indicated.

- Refer to FM (AG) - FM Approval Guide, UL (DIR),

- Perform Work in accordance with local authorities having jurisdiction, municipality, and water utility requirements.

- DELIVERY, STORAGE, AND HANDLING

- Accept valves on site in shipping containers with labeling in place. Inspect for damage.

- Provide temporary protective coating on cast iron and steel valves.

- Provide temporary end caps and closures on piping and fittings. Maintain in place until installation.

- Protect piping systems from entry of foreign materials by temporary covers, completing sections of the work, and isolating parts of completed system.

- FIELD CONDITIONS

Do not install underground piping when bedding is wet or frozen.

- WARRANTY

See Section 21 05 00, Common Work Results for Fire Suppression

PART 2 PRODUCTS

- GENERAL

- All system components, fittings and valves shall have pressure rating not less than 12.1 bar or

- times the system pressure whichever is greater.

- WATER PIPE

- Steel Pipe and Fittings for above ground installation:

- Pipe: Standard weight, schedule 40, listed, ASTM A53/A53M, seamless. Pipes used for drainage of pressurized network and pipes installed in the pump room shall be hot dipped galvanized. All other pipes shall be black steel.

- Fittings and joints for sizes up to 50mm: Threaded comply with ASME B16.4, Class 150

- Mechanical Grooved Couplings shall be used for pipe sizes 65mm and greater: Malleable iron housing clamps to engage and lock, "C" shaped elastomeric sealing gasket, steel bolts, nuts, and washers; galvanized for galvanized pipe.

- Mechanical Formed Fittings shall be used for pipe sizes 65mm and greater: Carbon-steel housing with integral pipe stop and O-ring pocked& O-ring uniformly compressed into permanent mechanical engagement onto pipe.

- After installation, all non-galvanized ferrous surfaces to be wire brushed and painted with one coat of red oxide paint and finished with red glossy paint.

- HDPE Pipe PN 16 pipes and fittings for site work installation:

- VALVES

- Valves: Manufacturer's name and pressure rating marked on valve body.

- Water Pressure Reducing Valves:

1.	40 DN (1-1/2 NPS) up to and including 200 DN (8 NPS):

- Function: Reduce higher inlet pressure to an adjustable, constant lower outlet pressure independent of flow rate fluctuations.

- Pilot-Operated Type: External pilot control.

- Construction:

- Listed.

- Body: Ductile iron conforming to ASTM A536, Grade 65-45-12.

- Internal Ferrous Materials: Coated with 0.10 mm (4 mils) of epoxy.

- External Surfaces: Coated with 0.10 mm (4 mils) of epoxy followed by coat of fire red enamel paint.

- Main Valve Seat Ring: Bronze, conforming to ASTM B61.

- Stem: Stainless Steel.

- Elastomers (diaphragms, resilient seats, and O-rings): Buna-N.

- Pilot Control System: Bronze, conforming to ASTM B61, with stainless steel trim.

- Gravity (Swing) Check Valve, Grooved End:

- 65 DN (2-1/2 NPS) up to and including 150 DN (6 NPS):

- Construction:

- Listed.

Body: ASTM A48/A48M gray iron, ASTM A126 cast iron, ASTM A536 cast iron.

- Coatings (as applicable): Rust inhibiting orange enamel paint on exterior and interior surfaces.

- Clapper:

- Material: Constructed of stainless steel or ductile iron

- Facing: EPDM.

- Seat: Constructed of stainless steel, brass or bronze

- Spring: Stainless steel.

- Hinge Pin: Stainless steel.

- Maximum Working Pressure: 1725 kPa (250 psi).

- FIRE DEPARTMENT CONNECTIONS:

- Fire department connections/ breeching inlet shall be a single face plate with two and/or four way as indicated on the drawings, 65 DN (2-1/2 inch) swivel fittings, internal threaded. Thread size and inlets according to NFPA 1963 or Authority Having Jurisdiction. Brass caps with gaskets, chains, and lugs.

- Finish: Chrome finish in compliance with Authority having jurisdiction.

- Rated Working Pressure: minimum 1200 kPa (175 psi) or system pressure or authority having jurisdiction whichever is greater.

- Signage: Raised or engraved lettering 25.4 mm (1 inch) minimum indicating system type according to AHJ.

PART 3 EXECUTION

- EXAMINATION

A. Verify that building service connection and municipal utility water main size, location, and invert are as indicated.

- PREPARATION

Cut pipe ends square, ream pipe and tube ends to full pipe diameter, remove burrs.

Remove scale and dirt on inside and outside before assembly.

Prepare pipe connections to equipment with flanges or unions.

- TRENCHING

- Hand trim excavation for accurate placement of pipe to elevations indicated.

- Form and place concrete for pipe thrust restraints at each change of pipe direction. Place

concrete to permit full access to pipe and pipe accessories. Provide suitable sq m ( or	sq feet)

thrust restraint bearing on subsoil.

- Backfill around sides and to top of pipe with cover fill, tamp in place and compact, then complete backfilling.

- INSTALLATION

A. General Requirements:

- Location of Water Lines:

- Terminate the work covered by this Section at a point approximately 1.5 m (5 feet) from the building unless indicated otherwise.

- Do not install water line closer horizontally than 3 m (10 feet) from any sewer line unless indicated otherwise.

- Water Piping Parallel With Sewer Piping:

- Install water piping minimum 3 m (10 feet) horizontally (measured edge-to-edge) from a sewer or sewer manhole where possible.

- Bottom (Invert) of Water Piping:

- Minimum 450 mm (18 inches) above top (crown) of sewer piping.

- Where this vertical separation of 450 mm (18 inches) above top (crown) of sewer piping cannot be obtained, the installation will be acceptable only when sewer piping is constructed of AWWA approved water pipe and pressure tested in place without leakage prior to backfilling.

- Sewer manhole must be of watertight construction and tested in place.

- Water Piping Crossing Sewer Piping:

- Crossing Under:

- Where water lines cross under gravity sewer lines, encase sewer line fully in concrete for a distance of at least 3 m (10 feet) on each side of the crossing, unless sewer line is made of pressure pipe with rubber gasketed joints and no joint is located within 900 mm (3 feet) horizontally of the crossing.

- Crossing Over:

(a) Install water lines which cross over sewer force mains and inverted siphons at least 600 mm (2 feet) above these sewer lines; when joints in the sewer line are within 900 mm (3 feet) horizontally from the water line, encase joints in concrete.

- Provide a separation of at least 450 mm (18 inches) between the bottom of the water piping and the top of the sewer piping.

- When local conditions prevent a minimum, vertical separation as described above, use the following construction:

- Provide sewer piping passing over or under water piping constructed of AWWA approved ductile iron water piping, pressure tested in place without leakage prior to backfilling.

- Protect water piping passing under sewer piping by providing a vertical separation of at least 450 mm (18 inches) between the bottom of the sewer piping and the top of the water piping; adequate structural support for the sewer piping to prevent excessive deflection of the joints and the settling on and breaking of the water piping; and that the length, minimum 6.1 m (20 feet), of the water piping be centered at the point of the crossing so that joints are equidistant and located as far as possible from the sewer piping.

- Do not install water lines in the same trench with gas lines, fuel lines, electric wiring,

Or any other services.	.

- Do not install copper tubing in the same trench with ferrous piping materials.

- Do not install water piping through or to come into contact with any part of a sewer manhole.

- Where nonferrous metallic pipe crosses any ferrous piping, provide a minimum vertical separation of 300 mm (1 feet) between pipes.

- Sleeving:

- Sleeve water piping where piping is required to be installed within 900 mm (3 feet) of existing structures.

- Provide ductile iron, Schedule 40 black steel, sleeves.

- Fill annular space between pipe and sleeves with mastic.

- Install water pipe and sleeve without damaging structures or causing settlement or movement of foundations or footings.

- Pipe Laying and Jointing:

- Remove fins and burrs from pipe and fittings.

- Prior to placing in position, clean pipe, fittings, valves, and accessories, and maintain in clean condition.

- Provide proper facilities for lowering pipe sections into trenches.

- Dropping or dumping of piping, fittings, valves, or any other water line material into trenches is not permitted.

- Cut pipe in a neat workmanlike manner accurately to length established at the site and work into place without forcing or springing.

- Replace by one of the proper length any pipe or fitting that does not allow sufficient space for proper installation of jointing material.

- Wedging or blocking between bells and spigots will not be permitted.

- Install bell-and-spigot pipe with the bell end pointing in the direction of laying.

- Grade the pipeline in straight lines avoiding the formation of dips and low points.

- Support piping at proper elevation and grade.

- Secure firm, uniform support.

- Wood support blocking will not be permitted.

- Install pipe so that the full length of each pipe section and each fitting will rest solidly on the pipe bedding; excavate recesses to accommodate bells, joints, and couplings.

Provide anchors and supports where indicated, necessary, and requested by engineer for fastening work into place.

- Provide proper provisions for expansion and contraction of pipelines.

- Keep trenches free of water until joints have been properly made.

- Close open ends of piping temporarily with wood blocks or bulkheads at the end of each work day.

- Do not install pipe during unacceptable trench conditions or inclement weather.

- Minimum Depth of Pipe Cover: Not less than 760 mm (2-1/2 feet).

- Connections to Existing Water Lines:

- Make connections to existing water lines only after receiving approval from the Architect/Engineer.

- Ensure minimal interruption of service on the existing line.

- Make connections to existing lines under pressure in accordance with the recommended procedures of the manufacturer of the pipe being tapped.

- Penetrations:

- Provide ductile-iron, Schedule 40 black steel, for pipes passing through walls

of valve pits and structures.

- Fill annular space between sleeves and walls with rich cement mortar.

- Fill annular space between pipe and sleeves with mastic.

- Special Requirements:

- Polyethylene (PE) Plastic Piping:

- Jointing: Comply with ASTM D2657, Technique I-Socket Fusion, Technique II-Butt

Fusion, or as approved by engineer.

- Offsets: Maximum allowable offset in alignment between adjacent pipe joints to be as recommended by the manufacturer and approved by the Architect/Engineer, not-to-exceed 5 degrees.

- Steel Piping:

a. Jointing:

- Welded: Make welded joints in accordance with AWWA C206 and install in

accordance with AWWA M11.

- Sleeve-Type Mechanical Coupling: Assemble sleeve-type mechanical coupling

joints in accordance with the coupling manufacturer's recommendations.

- Flanged:

- Make flanged joints up tight; avoid undue strain on flanges, fittings, valves, and other equipment and accessories.

- Align bolt holes for each flanged joint.

- Use full-size bolts for the bolt holes; use of undersized bolts due to misalignment of bolt holes or for any other purpose will not be allowed.

- Do not allow adjoining flange faces to be out of parallel to such a degree that the flanged joint cannot be made water-tight without straining the flange.

- When flanged pipe or fitting has dimensions that do not allow the making of a proper flanged joint as specified, replace it with one of correct dimensions.

- Grooved:

- Make grooved type joints with the couplings specified for this type joint connecting pipe with roll-grooved ends or pipe with welded-on cut-grooved adapters, each with dimensions as previously specified for this type of joint.

- Groove pipe ends in the field only with approved groove rolling equipment and groove adapters in the field only with approved groove cutting equipment; use only groove rolling and groove cutting equipment designed especially for the purpose and produced by a manufacturer of grooved joint couplings.

- Obtain approval for field-cut grooves prior to assembling the joint.

- Shouldered: Make shouldered type joints with the couplings specified for this type joint connecting pipe with the shouldered ends specified for this type of joint.

- Assemble grooved and shouldered type joints in accordance with the recommendations of the coupling manufacturer.

- Pipe Anchorage:

- Provide concrete thrust blocks (reaction backing) for pipe anchorage, except where metal harness is indicated.

- Thrust blocks to be in accordance with the recommendations for thrust restraint in AWWA M11, except that size and positioning of thrust blocks are to be as indicated.

- Use ASTM C94/C94M concrete having a minimum compressive strength of 15 MPa (2500 psi) at 28 days; or use concrete of a mix not leaner than one part cement, 2-1/2 parts sand, and 5 parts gravel, having the same minimum compressive strength.

- Metal Harness:

- Provide in accordance with the recommendations for joint harnesses in AWWA M11, except as otherwise indicated.

- Fabricated by the pipe manufacturer and furnished with the pipe.

- Valves:

- Set valves on solid bearing.

- Center and plumb valve box over valve.

- Set box cover flush with finished grade.

- FIELD QUALITY CONTROL

- Field Tests and Inspections:

- Provide all labor, equipment, and incidentals required for field testing, except that water and electric power needed for field tests will be furnished as set forth in Section 01 5100 - Temporary Utilities.

- Conduct piping tests before joints are covered and after concrete thrust blocks have hardened sufficiently and at least 5 days after placing of concrete after concrete thrust blocks have hardened sufficiently, at least 5 days after placing of concrete, and

- Prior to hydrostatic testing, obtain approval from Architect/Engineer for proposed method for disposal of waste water from hydrostatic testing.

- The Architect/Engineer will conduct field inspections and witness field tests as specified in this Section.

- Fill pipeline 24 hours before testing and apply test pressure to stabilize system, using only potable water.

- Before final acceptance, provide a video record of all piping from the building to the municipal connection to show the lines are free from obstructions, properly joined and sloped.

- Test water piping in accordance with NFPA 13, where the additional water added to the system must not exceed the limits given in NFPA 13.

- Pressure test piping to 1.5 times the working pressure.

- If tests indicate Work does not meet specified requirements, remove Work, replace and retest at no cost to Employer/Owner.

- Prepare reports of testing activities.

- CLEANING

- Upon completion of the installation of water lines, and appurtenances, remove and haul away

all surplus material, including debris resulting from the work.

- CLOSEOUT ACTIVITIES

- Demonstrate proper operation of equipment to Employer/Owner's designated representative.

- Demonstration: Demonstrate operation of system to Employer/Owner's personnel.

- Use operation and maintenance data as reference during demonstration.

- Conduct walking tour of project.

- Training: Train Employer/Owner's personnel on operation and maintenance of system.

- Use operation and maintenance manual as training reference, supplemented with additional training materials as required.

- Provide minimum of two hours of training.

- Location: At project site.

END OF SECTION