- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Rigid steel conduit.

          - Plastic conduit.

          - Plastic duct.

          - Precast concrete manholes.

          - Handholes.

          - Underground duct markers.

          - Cast-in-place manhole accessories.

      - REFERENCES

        - The IEE Wiring Regulations, 17th Edition (2008).

        - BS 4568 Rigid Steel Conduits, Zinc Coated.

        - BS 6099-2.2 / IEC 614-2-2 U.P.V.C. Rigid Conduits.

        - Local Codes and Standards

        - Local Electrical / Telecom Service Provider Regulations and Requirements.

      - SUBMITTALS

        - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan

        - Product Data: Submit for the following:

          - Flexible metal conduit.

          - Liquid tight flexible metal conduit.

          - Nonmetallic conduit.

          - Flexible nonmetallic conduit.

          - Nonmetallic tubing.

          - Raceway fittings.

          - Conduit bodies.

          - Surface raceway.

          - Wire way.

          - Pull and junction boxes.

          - Handholds./manhole

        - Method Statement and Manufacturer's Installation Instructions: Submit application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements. Include instructions for storage, handling, protection, examination, preparation, and installation of Product.

        - Provide samples of all proposed parts, fittings, material, accessories, ..etc. together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents:

          - Record actual routing of ducts.

          - Record actual locations of manholes.

      - COORDINATION

        - Coordinate layout and installation of ducts, manholes, handholes, and boxes with final arrangement of other utilities, site grading, and surface features as determined in the field.

        - Coordinate elevations of ducts and duct-bank entrances into manholes, handholes, and boxes with final locations and profiles of ducts and duct banks as determined by coordination with other utilities, underground obstructions, and surface features. Revise locations and elevations from those indicated as required to suit field conditions and to ensure that duct runs drain to manholes and handholes, and as directed by Site Architect.

      - QUALIFICATIONS

        - Manufacturers: Firms regularly engaged in manufacture of electrical ducts / manholes of types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.

        - B.	Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - QUALITY ASSURANCE

        - Electrical ducts and manholes shall generally be manufacturer’s standard construction and materials.

      - DELIVERY, STORAGE AND HANDLING

        - During unloading of PVC pipes and other items for underground electrical services, rough handling shall be avoided. Chains or wire ropes may be used, provided they are suitably covered, to protect the pipes and other items from damage.

        - Unloading by mechanical means such as a crane or fork lift may be used where PVC pipes and other items for underground electrical services are delivered in bundles or in crates. However, consideration shall be given to the total weight and the lifting capacity of the mechanical equipment, and the observance of the statutory safety requirements.

        - PVC pipes and other items for underground electrical services shall not be dropped or thrown to the ground, knocked against other conduits or against sharp objects that any cause permanent damage.

        - In preparing for laying the pipes in trenches, the pipes and fittings may be unloaded along the trench direct from the back of a truck. Ducts and fittings should be unloaded on the side opposite to backfill. Fittings including end bells, couplings and other accessories such as solvent cement and lubricant shall be stored at the trench site under cover to prevent loss or damage.

        - When storing on site, PVC pipes and other similar items shall be placed a level surface and shall be supported to minimize distortion, and protected from direct sunlight. Horizontal supports of adequate width shall be spaced not more than 1.5 m center to center beneath pipes to provide continuous and even support.

        - Vertical side supports shall be provided at 3 m spacing on rectangular stacks. The maximum free height of such stacks shall not exceed 1.5 m.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed installations to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - Underground Electrical Services for LV electrical systems, external lighting, low current systems, grounding shall comprise of manholes, and handholes interconnected via concrete encased PVC pipes, direct buried PVC pipes or direct buried cable trenching; all as shown on the Drawings and mentioned in the Specifications or required on site for proper installation and maintenance of electrical systems.

        - Excavation of trenching, backfilling, compaction and general grading required for electrical works shall be carried out in accordance with the requirements given in civil works specs.

        - Any metal frames, covers, louvers, etc. related to the works described under this Section shall be carried out in accordance with the requirements given in Division 05.

        - Any cast in place concrete related to underground electrical services described under this Section shall be carried out in accordance with civil works specs.

      - DUCT BANKS

        - Duct banks shall be either direct buried type or concrete encased type, as applicable and required on site.

        - Heavy duty rigid PVC conduits shall be used for direct buried or concrete encased underground duct systems. PVC conduits and fittings shall comply with the requirements of Division 26.

        - PVC conduit shall be suitable for a temperature range of 4 C to 60 C. Conduits within the duct bank shall be supported on plastic interlocking spacers, at intervals of approximately 2.5 m. A 25 mm minimum separation, edge to edge, shall be maintained, both horizontally and vertically, between the ducts.

        - All duct banks shall have a 75 mm concrete cover on the top, sides, and bottom of the PVC ducts. Anchorage shall be used to hold the ducts in place while pouring the concrete encasement.

        - Where the duct bank enters a building below ground level, the conduit shall terminate in an appropriate fitting.  An end bell shall be used on conduits entering manholes.

        - After completion of the installation of cables in the duct bank, seal the ends of duct banks using special caulking compound of a putty-like consistency. It shall be workable with the hands at temperatures as low as 1.7 oC, and shall not slump up to a temperature of 149 oC. It shall not be harden significantly when exposed to air.

        - A run of conduit shall not contain more than the equivalent of four quarter bends.  Bends in conduit shall be made without reducing the internal diameter of the conduit.  The inside radius of the conduit bends shall not be less than one meter.

        - Matching end bells and plugs, constructed of high impact plastic, shall be provided throughout the duct bank at the ends and in manholes.

        - Each length of conduit shall be provided with one standard coupling.  Couplings shall have a center step to ensure proper seating.  Joints shall be made with the solvent cement as recommended by the conduit manufacturer.

        - Concrete encasement shall be class C20 concrete with 13 mm maximum size aggregate for all duct banks.  For warning purposes, a red dye shall be troweled into the top surface after pouring the concrete.

        - An expansion joint of 55 mm per 100 meters maximum shall be provided in the duct banks.  Additionally, a construction joint shall be installed if pouring of concrete is commenced any time after initial set of adjacent concrete.  Neither expansion nor construction joints shall be installed under a roadway.

        - For duct banks in stable soils, the soil below the duct bank shall be compacted to 90 % of maximum density to a minimum depth of 300 mm.  A dewatering system shall be used to lower the water table below the final excavation depth to eliminate disturbance of in-situ soil densities.

      - STUB-UPS

        - Stubs-up for electrical equipment connections and other requirements shall consist of either 100 mm or 150 mm diameter hot double-dipped galvanized rigid steel conduit entirely encased in concrete.

        - Rigid steel conduits and bends for stub-ups shall comply with the requirements of Division 26.

        - The bends for stub-ups shall be 90 degrees with a minimum radius of 1200 mm.

        - Bends for stub-ups shall serve as transition between PVC conduits embedded below grade and rigid steel conduit installed exposed on surface. Such bends shall be provided with a PVC steel coupling on one end and a threaded male or female adapter on the other end.

      - MANHOLES

        - Appropriate type and size of manholes shall be provided as shown on the Drawings or required on site in compliance with the requirements of Local Standards Organization, BS and Electricity supply authority or Telecom supplier regulations.

        - Manholes for communication and low current systems shall be constructed in accordance with the standard practice and requirements of Telecom Supplier Regulations.

        - A sump pit shall be built into the base slab directly beneath the manhole opening to collect and retain any water present in the manhole.  Periodic maintenance may be required since sump pumps will not be permanently installed.

        - The duct bank manhole/interface shall include an expansion joint to take up longitudinal movement due to expansion and construction of the duct bank.  This joint shall also act as water stop to prevent water from seeping inside the manhole.

        - The exterior of the manhole shall be waterproofed, with a bituminous coating in accordance with civil works.

        - Each manhole shall have two cable pulling irons opposite each duct bank entrance.

        - Access to deep manholes shall be through a chimney. Permanent ladders or rungs shall be installed, if required by the Engineer on site or shown on the Drawings.

        - Manholes shall be provided with earth-rods and cable supports as per the requirements of Local Standards Organization, BS or Electricity supply Authority.

        - The frames and covers of all manholes shall be heavy duty, cast iron, round with solid type gasket lids, and countersunk locking devices. Covers shall seal tightly and not rock, when installed.

      - HANDHOLES

        - Handholes may be formed either monolithically or built up to designed sizes by combining several concrete sections cast in various shapes and sizes.

        - Handholes shall be provided with cast iron covers, sumps, ground-rods, etc. as shown on drawings or required as per the requirements of Local Standards Organization, BS or other applicable standards. Section joints shall be grouted.

        - The frames and covers of all hand holes shall be heavy duty, cast iron, round with solid type gasket lids, and countersunk locking devices. Covers shall seal tightly and not rock, when installed.

      - EARTH ROD PITS

        - Earth rods pits shall be provided for all earth rods in accordance with the requirements of Division 26.

        - Earth rod pits shall be precast of either square or round section with cover.

        - The cover of earth rod pits shall have appropriate marking as approved by the site Engineer.

      - CONCRETE PADS

        - Concrete pads shall be provided for all pad mounted equipment.

        - Concrete pads shall be 150 mm high, unless otherwise indicated, complete with steel reinforcement and necessary bolts, anchors, etc. required for the proper installation of pad mounted equipment.

        - Structural calculations for concrete pads supporting heavy equipment shall be submitted for Engineer’s approval before commencement of work on site.

      - CABLE WARNING SIGNS AND TAPES

        - Where cables are directly buried, cable warning signs shall be installed to minimize the likelihood of damage to the cables by excavation.  These signs shall be suitable for mounting on a riser pole, substation fence or separate stakes to suit the installations.

        - Posts for cable warning signs shall be placed as close to the cable as practical, but not closer than 900 mm horizontally from the cable.

        - Cable warning tapes shall be provided in accordance with the requirements given in Section 26 05 19. Tapes shall be placed at least 300 mm above the buried cables, and shall cover full width of the cable trench.

- EXECUTION

      - INSPECTION

        - Establish and propose exact routes and requirements of underground electrical services for approval of the Engineer, after co-ordination with all other existing or new underground services, before commencement of the work on site.

        - Examine the areas and conditions under which the underground electrical services are to be installed, and correct any unsatisfactory conditions detrimental to the proper and timely completion of the work. The Contractor shall not proceed with the work until all unsatisfactory conditions have been corrected in a manner acceptable to the Engineer.

      - EXCAVATION AND BACKFILING

        - The direct buried PVC ducts shall have a minimum dry sand cushion of 150 mm and a minimum dry sand cover of 300 mm, over which 50 mm thick concrete tiles shall be placed.

        - Depth for direct buried PVC ducts and PVC coated rigid steel conduits shall not be less than 600 mm from finished grade level to the top of conduits.

        - Top of concrete encased duct banks shall be installed 600 mm minimum below finished grade and shall connect manholes and hand holes as shown and required on site. Where a duct bank connects to a building, adapt the duct bank, at one meter beyond the building exterior wall, to the building conduit with the required couplings.

        - The concrete encasement surrounding the duct bank shall be rectangular in cross-section, having a minimum concrete thickness of 75 mm beyond any surface of the conduit.  Interlocking spacers shall be used to secure a uniform spacing between conduits of not less than 75 mm.

        - Trenches and duct banks shall be graded so that conduits will have a fall of at least 75 mm per 30 m towards the lower manholes or from the high point of the section towards the manholes or from the building towards a manhole.

        - Changes in direction of duct bank runs shall be accomplished by using special couplings limited to 5 degrees and/or 45 degrees bends having a 1 m radius sweep with straight sections of ducts between changes of direction and `S' sweep sections having a minimum of 500 m offset.

        - Where duct bank enters manholes, conduits shall terminate in end bells. Clean each conduit thoroughly before laying. During construction and after completion of the duct banks, plug the ends of conduits to prevent water washing mud into the conduits. Take particular care to keep the conduits clean of concrete or any other substance during the course of construction.

        - Securely anchor duct and brace with intermediate and base plastic spacers to prevent movement during the placement of concrete.

        - After the completion of portion of duct bank, a mandrel not less than 300 mm long, with a diameter of approximately 6 mm less than the inside nominal diameter of the conduits shall be pulled through each conduit, after which a brush with stiff bristles shall be pulled through to make certain that no particles of earth, sand or gravel have been left in the line. This cleaning shall be done one day after the concrete has been poured.

        - Install a nylon rope in each conduit after cleaning, after which the conduits shall be capped/ plugged immediately.

        - All duct banks shall enter manholes through rectangular openings of suitable dimensions provided in walls.  Such holes shall be sized to properly receive the duct, but shall not be too large for proper caulking.  The space between duct banks and manhole walls shall be caulked tight with lead wool.

      - STUB –UPS INSTALLATION

        - Comply with relevant requirement of Section 26 05 33.

        - Exact stub-ups locations and termination requirements for each equipment shall be verified on site, before commencement of lying underground or under floor PVC conduits for required power and control wiring.

        - Where extensions of PVC conduits above grade are required as stub-ups, a transition bend having PVC/Steel coupling on one end and threaded male or female adapter on the other end shall be used.

        - The PVC coated rigid steel transition bend or conduit shall extend minimum 150 mm above grade. A concrete envelope 100 mm high above the finished floor shall be formed around such risers to minimize corrosion at point of emergence. The top of the envelope shall be sloped for drainage.

      - CONSTRUCTION OF MANHOLES AND HANDHOLES

        - Manholes and hand holes shall be constructed of precast or cast-in situ concrete to sizes shown on the Drawings. Horizontal concrete surfaces of floors shall have a smooth steel trowel finish.

        - Frames and covers shall be watertight and covers shall fit the frames without undue play. These shall be free from warp and blow holes that may impair their strength of appearance.

        - Steel and iron shall be formed to shape and size with sharp lines and angle and shall have a smooth finish.

        - Provide all necessary lugs and brackets.

        - Set pulling-in irons and other built-in items in place before pouring concrete.

        - Provide a 3 m earth rod external to each manhole and hand hole. Also provide an earth bar in each manhole and handhold affixed to the wall above the duct bank box-outs. Connect to earth rod using 95 mm² solid round hot dip galvanized steel conductor and bond earth conductors associated with each power cable inside the manhole or hand hole.

      - GROUNDING

        - Ground underground ducts and utility structures according to Division 26 Section "Grounding and Bonding for Electrical Systems."

      - FIELD QUALITY CONTROL

        - Perform the following tests and inspections and prepare test reports:

          - Demonstrate capability and compliance with requirements on completion of installation of underground ducts and utility structures.

          - Pull aluminum or wood test mandrel through duct to prove joint integrity and test for out-of-round duct. Provide mandrel equal to 80 percent fill of duct. If obstructions are indicated, remove obstructions and retest.

          - Test manhole and handhole grounding to ensure electrical continuity of grounding and bonding connections. Measure and report ground resistance as specified in Division 26 Section "Grounding and Bonding for Electrical Systems."

        - Correct deficiencies and retest as specified above to demonstrate compliance.

      - CLEANING

        - Pull leather-washer-type duct cleaner, with graduated washer sizes, through full length of ducts. Follow with rubber duct swab for final cleaning and to assist in spreading lubricant throughout ducts.

        - Clean internal surfaces of manholes, including sump. Remove all foreign materials

- END OF SECTION