- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Uninterruptible Power Supply (UPS) System including, but not limited to, the following:

            - UPS cubicles/modules.

            - Static by-pass transfer switch.

            - Battery.

            - Accessories.

- Regarding the batteries autonomy for the UPSs will be as “HTM 06-01 Part A, 10.9. as follow:

- Double-conversion UPS units are most commonly used for TPS to dedicated final circuit outlets, used for example in clinical risk Category 4 or 5 areas.

- The most usual application of a double-conversion UPS is to provide tertiary power to IPS systems, particular those for the IEC 60364-7-710 Group 2. The batteries maintain an electrical supply following an outage of the PPS and prior to the SPS standby generators becoming available.

- Where the UPS battery provides TPS to nonoperating-theatre low-power applications, the battery autonomy should provide clinical staff with enough time to start “hand bagging” or connecting supplementary equipment battery packs. Consequently, battery autonomy of 15 minutes will be appropriate. Where the UPS battery provides tertiary power to operating theatre low-power applications, the battery autonomy should provide operating theatre staff enough time to facilitate “patient closure” for all theatre cases. Consequently, battery autonomy of 60 minutes will be appropriate.

      - REFERENCES

        - The UPS and all associated equipment and components shall be manufactured in accordance with the following relevant IEC standard:

          - IEC 60146 Semiconductor Convertors

          - IEC 6 1439-2 Low-voltage Switchgear and Control gear Assemblies. IEC 60204-1 Electrical Equipment of Industrial Machines.

          - IEC 60529 Protection Enclosure Degree

          - IEC 60076 Power Transformers

          - IEC 60950 Safety of Electrically Energized Office Machines, Data Processing Machines.

          - IEC 60364 Building Electrical Installation

          - IEC 60038 Standard Voltages

          - IEC 60068-2-32 Free Fall Testing

          - VDE 0510 Part 2 paragraph 6.5 Ripple Current for Battery Systems

          - EN 50091-1 Uninterruptible Power Systems “general and safety requirements” ISO9001

          - Local Codes, Standards and Regulations.

      - SUBMITTALS

        - Submit Manufacturer's illustrated leaflets, drawings, and technical data covering the equipment required.

        - Shop Drawings: Submit dimensioned drawings of UPS, batteries, battery racks, etc., which show accurately scaled equipment layouts, wire/cable routing and connections between UPS and batteries, single line diagram indicating metering, control; heat rejection and air flow requirements.

        - Submit product data for major component, such as batteries. Include catalogue sheets and technical data sheets with physical data and electrical performance.

        - Spare parts list.

        - Manufacturer's detail drawings consisting of a complete list of equipment and materials, manufacturer's descriptive and technical literature, battery sizing calculations, installation instructions, single-line diagrams, ladder-type schematic diagrams, elevations, layout drawings, and details required to demonstrate that the system has been coordinated and will function properly as a unit.

        - Factory and field test reports in booklet form tabulating factory and field tests and measurements performed, upon completion and testing of the installed system. Factory and field test reports shall be signed by an official authorized to certify on behalf of the manufacturer of the UPS system that the system meets specified requirements.

        - Six complete copies of operation and maintenance manuals outlining the step-by-step procedures required for system startup, operation and shutdown.  The instructions shall include the manufacturer's name, equipment model number, service manual, parts list, and brief description of equipment and its basic operational features.  Six complete copies of maintenance manuals listing routine maintenance procedures, possible breakdowns and repairs, and troubleshooting guides.  Corrective maintenance procedures shall identify the most probable failures and the appropriate repairs. Test measurement levels shall be referenced to specific test points on the installed equipment. Operation and maintenance manuals may be either combined or separate.

        - Lesson plans and training manuals for the training phases, including type of training to be provided and proposed dates, with a list of reference materials.

        - Method Statement for installation, testing, commissioning and operation of proposed systems.

        - It's the contractor's responsibility to get his system proposal approvals without any extra time extension.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: Submit description of operating procedures; servicing procedures; list of major components; recommended remedial and preventive maintenance procedures; and spare parts list.

      - QUALIFICATIONS

        - Manufacturer’s: Firms regularly engaged in manufacture of UPS equipment, whose products have been in satisfactory use in similar service for not less than 10 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with UPS equipment installation similar to that required for project.

      - QUALITY ASSURANCE

        - UPS equipment shall comply with the requirements of BS, IEC and Local Standards.

      - DELIVERY, STORAGE AND HANDLING

        - Pack all equipment for protection during transportation.

        - Store in a dry, clean location.

        - Do not install equipment until it can be protected from damage during construction.

      - MAINTENANCE MATERIALS

        - Provide maintenance materials under provisions of Section 01 92 00 – Closeout Procedures.

        - Provide a complete set of spare parts for UPS as recommended by the manufacturer.

        - Furnish one set of tools required for preventative maintenance of the UPS system. Package tools in adequately sized metal tool box.

      - SPARE PARTS

        - Furnish under provisions of Section 01 92 00 - Closeout Procedures.

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Fuses: Five of each type and rating used.

          - Indicating Lights: Four of each type installed.

          - Touchup Paint: Two containers of paint matching enclosure finish, each 250 mL.

          - Protection relays: one of each type.

          - Circuit Boards of critical circuit: one of each type.

        - Maintenance Tools: Furnish tools and miscellaneous items required for test,
inspection, maintenance, and operation.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide (12) months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of (1) year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - The UPS and battery system shall be capable of withstanding the harsh environmental and ambient conditions as described in Section 26 05 00 without mechanical or electrical damage or degradation of operating characteristics.

        - Sound pressure levels produced by the UPS, when operating under full rated load, at a distance of 1.5 m in any direction from the perimeter of the unit, shall not exceed 65 dB as measured on the A scale of a standard sound level meter at slow response. Acoustical treatment of the UPS room, when required, shall be carried out in as called for in the tender documents.

      - SYSTEM DESCRIPTION

        - The UPS used shall be with reverse transfer designed for capacity expansion by addition of parallel modules in the field with minimal downtime. The UPS module shall be capable of being upgraded for additional capacity to the largest model's power rating by the manufacturer on site without changing any power components or increasing the physical size of the module.

        - As a minimum, the following components shall be provided:

          - Battery.

          - Rectifier/charger with capacity sufficient to supply full load to inverter while recharging fully discharged battery to 95% of full capacity in four hours or less; and within the input current limits specified.

          - Inverter to provide power to load during normal operation.

          - Static switch to transfer the critical load to the by-pass AC input source without interruption. The load shall be gradually transferred back to the inverter output, either manually or automatically, without interruption, once the inverter has been synchronized to the by-pass source.

          - External Manual switch to bypass static switch for maintenance to isolate the rectifier/charger, inverter and static switch while continuing to supply power to the load via the by-pass AC input source. Transfer to the manual switch shall be without interruption to the load.

      - EQUIPMENT RATINGS/CHARACTERISTICS

        - UPS Power Rating:

          - The continuous power rating of the UPS shall be, in no case less than that shown on the Drawings or mentioned in BoQ. It shall meet all the criteria specified herein to fulfill the power demand of the loads fed by UPS as shown on the Drawings.

          - The continuous power rating shall be over entire battery voltage range at specified power factor.  It shall maintain output voltage within specified limits at any load from full load to no-load.

        - Battery Capacity:

          - Battery shall be capable of operating at full load for 15 minutes without any voltage drop and 1/2 hr. for critical loads and / or as indicated on drawings & BOQ as well.

          - Discharge time to end voltage:  10 minutes, at 25 C. Battery shall be capable of delivering 125% of full rated UPS load at initial start-up.

        - Input Voltage:

          - Rating: 400 V, 3 phase or as shown on the Drawings.

          - Operating Range: Plus 10% or Minus 15%.

        - Input Frequency:

          - Rating: 60 Hz.

          - Operating Range: + 3 Hz.

        - Input Current:

          - Maximum Limit: Adjustable to maximum of 125% of that required to operate at full load with battery bank on float charge.

          - Current Walk-in:  25 to 100% in fifteen seconds.

        - UPS Power Factor:

          - The power factor over full range of loads and input voltages shall be in the range of 82 to 100%, lagging.

        - Total Harmonic Current Distortion:

          - The maximum harmonic current distortion of input current wave form shall be 10% at full load.

        - Output Voltage:

          - Configuration: Three phase, 4-wire plus earth, 400 V or as shown on the Drawings.

          - Regulation:

            - + 0.5% for balanced load, full range of DC input and no load to full load variations.

            - + 3% for 50% unbalanced load, full range of DC input and no load to full load variations.

            - +10% during maximum overload of the system.

          - Adjustment: + 5%.

        - Output Frequency:

          - Rating: 50 Hz.

          - Operating Range: + 0.1%.

          - Slew rate: 1.0 Hz per second maximum

        - Output Power Rating: As shown on the Drawings, at 0.9 lagging pf.

        - Output Current:

          - Shall not exceed 150% of rated output current.

        - Phase Displacement:

          - Balanced load: + 1 o of by-pass input.

          - 50 % load imbalance phase-to-phase: + 3 o of by-pass input.

        - Bypass Line Synchronizing Range:

+ 0.5 Hz

+ 1.0 Hz 		Switch Selectable

+ 3.0 Hz

        - Load Power Factor Range: 1.0 to 0.8 lagging

        - Overload capability: At full voltage and excluding battery shall be as follows:

          - 125 % load for 10 minutes.

          - 150 % load for 30 seconds.

          - 300 % load for one cycle after which it shall be current limited to 150 % until fault is cleared or UPS goes to bypass.

        - Voltage Transient Response:

          - 20 % load step: + 4%.

          - 30 % load step: + 5%.

          - 50 % load step: + 8%.

          - Loss or return of AC input power: + 1%.

          - Manual Transfer of 100 % load: + 4%.

          - Automatic transfer of load to bypass: + 4%.

        - Transient Recovery Time: To within 1 % of output voltage within 20 ms.

        - Voltage Unbalance:

          - Balanced Load: + 1%.

          - 20 % unbalanced load: + 1%.

          - 50 % unbalanced load: + 2%.

          - 100 % unbalanced load: + 5%.

        - Output Harmonic Distortion: At rated frequency and voltage, from 10 % load to full load and over entire battery voltage range, when measured into a linear load with a crest factor of less than 3 to 1, the output harmonic distortion shall be:

          - For any single harmonic:  maximum 3%.

          - Total rms harmonic distortion:  maximum 5%.

        - Efficiency: Not less than 92% at full load and half load including battery and isolation transformer losses.

        - The efficiency of UPS system including battery and isolation transformer losses shall be not less than 92% at full load and half load.

      - UPS MODULE

        - UPS module shall consist of a rectifier/charger unit and a 3-phase inverter unit with their associated transformers, synchronizing equipment, protective devices and accessories as required for operation.

        - Rectifier/charger unit shall be solid state and shall provide direct current to the DC bus.

        - Rectifier/charger unit shall be provided with an input protective device.  The protective device shall be sized to accept simultaneously the full-rated load and the battery recharge current. The protective device shall be capable of shunt tripping and shall have symmetrical interrupting capacity as required.  The protective device shall have provision for locking in the "off" position.  A surge suppression device shall be installed at the UPS input to protect against lightning and switching surges.

        - A dry-type, isolated-winding power transformer shall be used for the rectifier unit. The transformer's hottest spot winding temperature shall not exceed the temperature limit of the transformer insulation material when operating at full load.  The transformer insulation shall be Class H, 150 C rise. Transformer connections shall be accessible from the front.  If IGBT technology rectifier is used then the input transformer is not required, however the output transformer should be an integral part of the UPS and the THDi should be less than 3%.

        - Rectifier/charger unit shall be protected by a power walk-in feature such that when AC power is returned to the AC input bus, the total initial power requirement will not exceed 20 % of the rated full load current.  This demand shall increase gradually to 100% of the rated full load current plus the battery charging current over the specified time interval.

        - Rectifier/charger unit shall be sized for the following two simultaneous operating conditions:

          - Supplying the full rated load current to the inverter.

          - Recharging a fully-discharged battery to 95% of rated ampere-hour capacity within ten times the discharge time after normal AC power is restored, with the input protective device closed.

        - Primary current limiting:  Battery-charging current shall be voltage regulated and current limited.  The battery-charging current limit shall be separately adjustable from 2 % to 25 % of the maximum discharge current.  After the battery is recharged, the rectifier/charger unit shall maintain the battery at full float charge until the next operation under input power failure.  Battery charger shall be capable of providing equalizing charge to the battery.

        - Rectifier/charger unit shall have an output filter to minimize ripple current supplied to the battery; the ripple current into the battery shall not exceed 3% RMS.

        - Rectifier/charger unit shall have manual means for adjusting DC voltage for battery equalization, to provide voltage within plus 10% of nominal float voltage.

        - Module shall have a DC protective device to isolate the module from the battery system.  The protective device size and interrupting rating shall be as required by system capacity and shall incorporate a shunt trip as required by circuit design.  The protective device shall have provision for locking in the "off" position.

        - Inverter unit shall be a solid-state device capable of accepting power from the DC bus and providing AC power within specified limits.

        - The inverter shall be able to sustain an overload as specified across its output terminals.  The inverter shall not shut off, but shall continue to operate within rated parameters, with inverse-time overload shutdown protection.

        - The inverter shall normally operate in phase-lock and synchronism with the bypass source.  Should the bypass source frequency deviate beyond 60 Hz by more than 0.5 Hz, the internal frequency oscillators contained in the power module shall be used to derive the new frequency reference.  Upon restoration of the bypass source within the required tolerance, the inverter shall resynchronize with that source at a slew rate not exceeding the specified limits. The design of the oscillator and synchronizing circuits shall be such that failure of any associated component, connector pin, terminal lead wire or DC power source in either the open or shunted mode shall affect only one inverter leg.  Such failure shall not cause transient disturbance of the critical load in excess of the stated limits.

        - Electronic controls shall be incorporated to provide individual phase voltage compensation to obtain phase balance.

        - Each control logic printed circuit board shall be electrically and physically packaged on an individual plug-in module with separate indication and adjustments.

        - The control logic shall include status indicators for trouble-shooting the control circuits.  These indicators shall be mounted on the circuit card edge or face such that they will be visible without repositioning the card, and shall be labeled with the function name.

        - The output protective device shall be capable of shunt tripping and shall have interrupting capacity as specified.  Protective device shall have provision for locking in the "off" position.

        - The inverter output transformer shall be similar to the input transformer and shall be capable of handling up to K-13 nonlinear loads as described in IEEE C 57.110.

        - UPS module shall have built-in self-protection against under voltage, overvoltage, over current and surges introduced on the AC input source and/or the bypass source.  The UPS system shall sustain input surges without damage.  The UPS shall also have built-in self-protection against overvoltage and voltage surges introduced at the output terminals by paralleled sources, load switching, or circuit breaker operation in the critical load distribution system.

        - UPS module shall be self-protected against over current, sudden changes in output load and short circuits at the output terminals.  UPS module shall be provided with output reverse power detection which shall cause that module to be disconnected from the critical load bus when output reverse power is present.  UPS module shall have built-in protection against permanent damage to itself and the connected load for predictable types of failure within itself and the connected load.  At the end of battery discharge limit, the module shall shut down without damage to internal components.

        - An RS 232 C communications and data acquisition port shall be provided.  This port shall allow the system parameters, status, alarm indication and control panel functions specified to be remotely monitored.

        - The UPS units and breakers to be controlled and monitors by BMS. The contractor to provide the UPS sequence of operation and breakers logic considering (Cat. 5) load .

      - STATIC BY-PASS TRANSFER SWITCH

        - A static by-pass transfer switch shall be provided as an integral part of the UPS which shall consist of a static switch and a by-pass protective device or by-pass switch.  The control logic shall contain an automatic transfer circuit that senses the status of the inverter logic signals and alarm conditions and provides an uninterrupted transfer of the load to the by-pass AC power source, without exceeding the transient limits specified herein, when a malfunction occurs in the UPS or when an external overload condition occurs.  The power section of the static by-pass transfer switch shall be provided as a plug-in type assembly to facilitate maintenance. The static by-pass transfer switch shall be used to connect the by-pass AC power source or the UPS inverter output to the critical load when required.

        - The static by-pass transfer switch shall automatically cause the by-pass AC power source to assume the critical load without interruption when the by-pass control logic senses one of the following conditions and the UPS inverter output is synchronized to the by-pass AC power source:

          - Inverter overload exceeds unit's rating.

          - Battery protection period is expired and bypass is available.

          - Inverter failure.

        - If an overload occurs and the UPS inverter output is not synchronized to the by-pass AC power source, the UPS inverter output shall current-limit for 200 milliseconds minimum.  The inverter shall then turn off and an interrupted transfer to the by-pass AC power source shall be made.  If the by-pass AC power source is beyond the conditions stated below, an interrupted transfer shall be made upon detection of a fault condition:

          - By-pass voltage greater than + 10% from the UPS rated output voltage.

          - By-pass frequency greater than + 0.5 Hz from the UPS rated output frequency.

          - Phase differential of AC bypass voltage to UPS output voltage greater than +3 o.

        - It shall be possible to make a manually-initiated static transfer from the system status and control panel by turning the UPS inverter off.

        - The static by-pass transfer switch shall automatically forward transfer, without interruption after the UPS inverter is turned "on", or after an instantaneous overload-induced reverse transfer has occurred and the load current has returned to less than the unit's 100 % rating.

        - The control logic circuitry shall provide the means of making a forced or reverse transfer of the static by-pass transfer switch on an interrupted basis.  Minimum interruption shall be 20 milliseconds when the UPS inverter is not synchronized to the bypass AC power source.

        - The static by-pass transfer switch shall withstand the following overload conditions:

          - 200% of UPS output rating for 5 minutes.

          - 125% of UPS output rating for 10 minutes.

      - UPS CABINET FABRICATION

        - The UPS cabinet shall be floor mounted, totally enclosed cubicle type in accordance with the requirements given in Section 26 24 13.

        - Electroplate brackets and securing hardware with corrosion resistant material.  Secure bolts, studs and nuts with lock washers.

        - Identify internal wiring at each end of conductor.  Provide cabinet grounding lugs.

        - Conversion Equipment Enclosure:  The enclosure shall allow access from front for servicing adjustments and connections.  Access hinged door equipped with tumbler lock and latch handle.  Equip cabinet for fork truck lifting.

        - Equip air inlet with permanent type filters and pressurize cabinet, or use gaskets around door and panel openings to prevent entry of dirt.

        - Exhaust fans must be provided

        - Cabinet finish:  Primed and painted inside and outside with suitable semi-gloss enamel.

      - BATTERY

        - Storage Battery:  Sealed lead acid designed for auxiliary power service.  Provide battery with impact resistant plastic case.  Provide cells with explosion proof vents, clear containers, and ample space for plate growth without stressing container and cover.

        - Electrolyte Specific Gravity:  No greater than 1.25 when full charged and measured at 25C.

        - Ampere-Hour Rating:  Sufficient to supply direct current to inverter for outage period specified, with inverter operating at full rated output, to a discharge limit of not less than 1.65 V per cell.

        - Battery Racks:  Maximum of three-tier, all steel construction, with plastic insulating rails at all points of contact with the battery case.  Paint racks with acid resistant paint.

        - The battery pack assembly shall be furnished in a battery cabinet matching the UPS cabinet.  The battery cabinet shall be designed to allow for checking the torque on the connections in the battery system and to provide adequate access for annual housekeeping chores.  External wiring interface shall be through the bottom or top of the assembly.  A smoke and high temperature alarm shall annunciate detection of either smoke or high temperature within the battery cabinet.

        - Each battery pack assembly shall have a fused disconnect switch provided in an enclosure, finished with acid-resistant paint and located in line with the assembly.  Switch shall be complete with line side and load side bus bars for connection to battery cells.  Switch shall be rated 3-pole with interrupting rating as required by system capacity, and shall have an external operator that is lockable in the "off" position.

        - A battery monitor shall be provided for each battery pack assembly.  As a minimum, this device shall monitor the following parameters:

          - Total system voltage.

          - Ambient room temperature.

          - Total battery discharge cycles with a duration of 30 seconds or less.

        - The monitor shall also record the total accumulated discharge minutes and accumulated battery system discharge kW hours.

      - CONTROLS AND INDICATORS

        - Controls: All standard controls and alarms as recommended by the manufacturer shall be provided, which shall include the following as a minimum:

          - AC input circuit breaker.

          - "Inverter operate" switch, to initiate inverter operation.

          - "Inverter standby" switch, to cause inverter to cease operation.

          - "Static switch transfer” switch, to permit manual actuation of static transfer switch.

          - "Static switch lock-out" switch, to inhibit automatic retransfer of load to inverter.

          - Battery charge timer.

          - "Indicator test" switch.

          - Static switch output circuit breaker.

          - Static switch output circuit breaker.

          - Static switch bypass circuit breaker.

          - Controls for maintenance bypass switch.

        - Indicators:  All standard indicators as recommended by the manufacturer shall be provided, which shall include the following as a minimum:

          - "Inverter synchronized to utility."

          - "Load connected to utility."

          - "Static transfer switch inhibited."

          - "High/low DC voltage."

          - "Over temperature."

          - "Inverter output overload."

        - Meters:  All standard meters as recommended by the manufacturer shall be provided, which shall include the following as a minimum:

          - Rectifier/charger DC voltage and current.

          - Utility, inverter output, and load AC voltage.

          - Load AC current.

          - Inverter output and utility frequency.

          - UPS output watts.

        - Selector switches for each phase of the AC valves shall be provided. All meters shall be rated for 1% accuracy class.

- EXECUTION

      - INSTALLATION

        - Install UPS system in accordance with manufacturer's written instructions and the requirements of Local Standards, BS and IEC.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - Verify specification performance criteria; measure battery discharge and recharge times; simulate fault in each system component and utility power; Operate the unit for eight hours; and other tests as recommended by the manufacturer.

      - MANUFACTURER'S FIELD SERVICES

        - Prepare and start systems.

        - Include services of technician to supervise adjustments, final connections, and system testing.

        - The services of a manufacturer's representative who is experienced in the installation, adjustment, and operation of the equipment specified shall be provided. The representative shall supervise the installation, adjustment and testing of the equipment. The representative shall check the wiring between equipment, start up the system, and field test the functions, interlocks and protective devices to ensure that the total system is functioning according to the intent of the design.  The field tests shall be performed under the supervision of a factory-trained representative of the equipment manufacturer and witnessed by the Engineer. The Engineer shall be given 2 weeks written advance notice of the date and time when testing will be conducted.

      - TESTING AND COMMISSIONING

        - Testing and commissioning of the complete UPS system shall be carried out by the UPS equipment manufacturers authorized specialist commissioning agent in the presence of the Architect.

        - Test certificates shall be issued in triplicate for all necessary tests performed to ensure complete and satisfactory operation of the UPS equipment.

- END OF SECTION