SECTION 22 05 53

IDENTIFICATION FOR MECHANICAL PIPING AND EQUIPMENT

PART 1 GENERAL

- Work Included

- Compliance with relevant General Requirements of Mechanical Services.

- Reference Standards

BS 381C	Specification for colors for identification, coding and special

purposes.

BS 729	Specification for Hot dip galvanized coatings on iron and steel

articles.

BS 1710:1980	Identification of pipelines and services.

BS 4652	Specification for metallic zinc-rich priming paint.

BS 4800	Paint colors for building purposes.

BS 5378 Part 1, Safety Signs and Colors - Specification for Color and Design HVCA DW 144 Specification for sheet metal ductwork.

- Submittals

- All materials submittals shall include a detailed, clause-wise, compliance statement.

- All materials submittals shall include detailed catalogues, product literature and descriptions of all equipment and fittings with selection charts, capacities etc.

- All material submittals shall include copies of relevant standards.

- Contractor shall submit samples of each type of identification for Consultant’s approval.

PART 2 PRODUCTS

- IDENTIFICATION APPLICATIONS

Automatic Controls:  Tags.  Key to control schematic.

Control Panels:  Nameplates.

Heat Transfer Equipment:  Nameplates.

Instrumentation:  Tags.

Major Control Components:  Nameplates.

Piping:  Pipe markers.

Pumps:  Nameplates.

Relays:  Tags.

Small-sized Equipment:  Tags.

Tanks:  Nameplates.

Thermostats:  Nameplates.

Valves:  Tags and ceiling tacks where located above lay-in ceiling.

Water Treatment Devices:  Nameplates.

- Pipe work Identification

- Primary Identification

Apply color bands, 300mm wide, in accordance with BS 1710, to each pipe at least once in every room or enclosed area; at intervals not exceeding fifteen meters; at every junction; at every valve; and at every inspection and access position into service shafts, false ceilings, bulkheads etc.

Color bands shall not be provided on pipes which are to be painted to match internal decorations.

Where two or more pipes run in parallel, then the color banding for each pipe shall be at the same locations.

At intervals as for color banding, colored arrows and wording shall be stenciled to the insulation or pipe work to indicate direction of flow, and to indicate the circuit or system.

- Secondary Identification

Apply color bands, 50mm wide, in accordance with BS 1710 and superimpose a legend identifying circuit, direction of fluid or gas flow, nominal pipe bore and, where appropriate, fluid or gas pressure.

Color bands shall not be provided on pipes which are to be painted to match internal decorations.

- All pipe work shall be colour coded in accordance with BS 1710 as detailed in Table 1.

Table 1: Identification of Pipelines

| Pipe contents | Color code indication (Approx 100 mm) | Basic Color (Approx 150 mm) |
| --- | --- | --- |
| Drinking Water | TO BS 1710 | Blue |
| Cold water Down Service | TO BS 1710 | Green |
| Hot Water Supply | TO BS 1710 | Green |
| Drainage | TO BS 1710 | Black |
| Refrigerant | TO BS 1710 | Yellow Ochre |

- Identification to pipe work shall consist of 100mm PVC adhesive bands over the basic colour and shall include flow direction arrows together with the abbreviation of the service name.  All coding requirements are to be agreed with the Engineer.

- Code indication for safety conditions shall be as follows:-

Safety Colour			    BS colour reference

BS 4800

Red					04  E  53

Yellow					08  E  51

Auxiliary Blue				18  E  53

Safety colour references are as follows: -

1.	Red for fire fighting equipment.

2.	Yellow with black diagonal stripes for warning of danger.

3.	Yellow with trefoil symbol for ironizing radiation

(as defined in BS 3510).

4.	Auxiliary blue in connection with green basic colours, to denote pipes carrying fresh water, either potable or non-potable.

Safety colour references shall be applied using 100mm wide sections of PVC adhesive band in all permanent locations, to be agreed with the Engineer.

Colour references shall include notation as follows: -

1.	FIRE

2.	DANGER

3.	RADIATION

4.	POTABLE OR NON-POTABLE

In the case of fire service, all equipment, i.e. valves, suction tanks, etc., shall also be painted red.

- Un-insulated pipe work shall be painted with one coat of undercoat and two coats of gloss finish to the relevant BS colour.

- Valve identification shall be by means of 40mm diameter traffalyte discs of white/black/white composition.  Letters and figures of 8mm minimum height, identifying the service and valve number shall be engraved into the material.  A 3mm diameter hole shall be drilled through the disc for the purpose of securing the disc to the valve.

- Plant identification shall be by means of traffalyte labels of white/black/white composition.  Letters and figures of 8mm minimum height identifying the plant shall be of a size to be agreed with the Engineer.  A minimum of two 3mm diameter holes shall be drilled through the label to the plant.

- All plants shall carry the manufacturer's identification plate which shall incorporate all details of electrical and mechanical duties.

- Ductwork Identification

- Standards

Generally color code and label to HVCA Specification DW 144 (Appendix B).

Duct Identification Colours

| Type | Colour | BS 4800 |
| --- | --- | --- |
| Conditioned Air Warm Air Fresh Air Exhaust / extract re-circulated air | Red and Blue Yellow Green Grey | 04353 / 18E53 10E53 14E53 AA009 |

- Primary Identification

Apply color bands, 300mm wide, to each duct at least once in every room or enclosed area; at intervals not exceeding fifteen meters; at every junction; at every damper; and at every inspection and access position into service shafts, false ceilings, bulkheads etc.

- Secondary Identification

For ducts with longest side or diameter up to and including 225mm. Paint color bands 50mm wide and superimpose legends.

For ducts with longest side or diameter over 225mm. Paint or apply transfers to identification triangles, or triangular plates. Superimpose or incorporate legends.

- Triangular Plates

Attach to buckle bands or stool pieces and fix to ducting, with apex indicating direction of airflow. Submit details of plates and fixings for approval before painting and marking. Use equilateral triangle of side 150mm minimum.

- Legends

Apply transfers of an approved type to color bands or triangles or triangular plates. Identify floor and space served, associated equipment reference and direction of airflow.

- Pipe work and Duct work Markings

In addition to the identification band coding all services shall be legibly and neatly marked with black letters where a light background is used and white letters where a dark background is used and appropriately colored triangles to indicate the direction of flow as follows & as requested by engineer on site:

Primary Chilled Water flow and return	P.CHW

Secondary Chilled Water flow and return	S.CHW

Chilled Water flow and return	CHW

Outside Air	OA

Return Air	RA

Exhaust Air	EA

Supply Air	SA

Mains Cold Water Service	MCW

Cold Water Service	CWS

Boosted Cold Water	BCW

Hot Water Services	HWS

Fire Water Services	FWS

- Plant and Equipment Identification General

Each of the MEP plant units and equipment shall be factory painted in accordance with the manufacturer's recommendations to a color designated and approved by the Consultant. Any damage to finishes which may have occurred during transit, storage, installation or otherwise shall be made good in the manner recommended by the manufacturer and to the satisfaction of the Consultant.

- Specification plates

Each unit shall have a specification metal plate (the manufacturer's name plate) which shall show full details as manufacturer's name, unit and unit motors serial numbers, model numbers, date of manufacture and BS or other number for the internationally approvable standard to which the item of plant conforms.

- Pumps:

Pump size, rpm, amperes, impeller diameter, lubricants, pump characteristics, flows for the duty specified, the K factor of the orifice plate if applicable, and any other pertinent information as may be required by the Consultant. This plate shall also be securely fixed to the pump.

- AHU-s, Fan Coils and Fans:

Air flows for the duty specified, fan size, rpm, amperes, impeller diameter, lubricants, fan characteristics, coil type and characteristics air and water inlet/outlet temperatures and any other pertinent information as may be required by the Consultant. This plate shall also be securely fixed to the fan. An engraved label shall be fixed to each filter stating the maximum permissible pressure drop.

The same as above is applicable to any other single piece of equipment or units within the MEP systems

- Identification plates

In addition to the specification plates, each unit shall be provided with an identification plate showing the code number for each unit as indicated on the system schematics. This plate shall be securely fixed to the unit in a prominent position.

- Plant And Equipment Identification, Engraved Plates

- Standards

Identify each item of equipment by name and, where appropriate, by agreed reference characters. Provide color identification as called for in work sections and, in all cases, color firefighting equipment red.

- Identification Colors

Use primary and secondary identification colors of associated system.

- Plates

Use rectangular metal or laminated plastic, securely fixed to each item of equipment.

- Lettering Engraved plates filled with paint.

- Legends

Engrave plates with an approved text. Incorporate operating duty of equipment where this is not incorporated in other labeling.

- Plant And Equipment Identification, Laminated Plates

- Standards

Identify each item of equipment by name and, where appropriate, by agreed reference characters. Provide color identification as called for in work sections and, in all cases, color firefighting equipment red.

- Identification Colors

Use primary and secondary identification colors of associated system.

- Plates

Use rectangular metal or laminated plastic, securely fixed to each item of equipment.

- Lettering

Laminated	plates,	multi-colored	with	outer	layer removed	for lettering.

- Legends

Engrave plates with an approved text. Incorporate operating duty of equipment where this is not incorporated in other labeling.

- Plant And Equipment Identification, Back Filled Perspex

- Standards

Identify each item of equipment by name and, where appropriate, by agreed reference characters. Provide color identification as called for in work sections and, in all cases, color firefighting equipment red.

- Identification Colors

Use primary and secondary identification colors of associated system.

- Plates

Use rectangular metal or laminated plastic, securely fixed to each item of equipment.

- Lettering

Clear per specs back filled to reveal lettering.

- Legends

Engrave plates with an approved text. Incorporate operating duty of equipment where this is not incorporated in other labeling.

- Valve and Cock Identification

A.     Standards

Identify each valve, cock, stop valve, air vent, drain cock etc. with disk engraved with   numerical reference. Except where exposed in occupied areas.

B.     Identification Colors

Use primary and secondary identification colors of associated system for painted or self    color discs.

- Discs and Labels

Securely attach metal or laminated plastic discs, minimum diameter 35mm, to each item. The labels for valves as alternatives shall be brass or Traffolyte plastic 80 mm by 40 mm with a hole 10 mm from one end. A short length of brass chain with a ring at each end shall be used to permanently attach the labels to each valve.

- Legends

Engrave discs with permanent characters, minimum height 10mm. Each label shall indicate the type of service and the valve reference number which shall agree with a schedule of valves which shall be prepared for each service. The schedule shall comprise the valve reference number, the function of the valve and its location.

Incorporate in operating instructions relating to regulating valves and flow measuring equipment, details of flow rate, pressure differential and setting, as appropriate.

- Air Volume Regulating And Control Damper Identification

A.             Standards

Identify each regulating and control damper. Except where exposed in occupied areas. On ductwork  dampers, clearly indicate commissioning set point.

Identification colors

B.         Use primary and secondary identification colors of associated system for painted or self  color  discs.

C.             Discs

Securely attach metal or laminated plastic discs, minimum diameter 35mm, to each item. Legends Engrave discs with permanent characters, minimum height 10 mm.

- Instrument Identification

A.             Standards

B.           		Identify each instrument by name and, where appropriate, by agreed reference  characters.

C.             Plates Use rectangular metal or laminated plastic, securely fixed to each instrument.

D.             Legends

E.             Engrave plates with an approved text.

- Danger And Warning Notices Hazardous Systems

A.   Color code and label hazardous systems and equipment to requirements of Health and Safety         Executive Guidance Notes.

B.     The warning flash as specified in BS 5378 Part 1, "Safety Signs and Colors - Specification for Color   and Design" shall be attached to all internal and external removable covers of electrical equipment and panels, which provide shielding from live conductors.

C.      Labels to be in both Arabic and English.

- System Identification Installation Charts, Perspex Glazed Frame

A.     System Schematics

Supply and fix a referenced schematic diagram (or diagrams) of all systems as installed, including   equipment and ancillary schedules. Show scheduled information on diagram.

B.      Identify all items by appropriate reference characters.

C.      Control Schematics

D.   Supply and fix a referenced schematic diagram (or diagrams) of all control systems as installed, including equipment and ancillary schedules. Show scheduled information on diagram.

E.      Identify all items by appropriate reference characters.

F.     Location Fix in each plant room or equipment room.

G.    Finish Perspex sheet glazing with surrounding frame and mounting attachments.

- System Identification Installation Charts, Acrylic Glazed Hardwood Frame

A.       System Schematics

Supply and fix a referenced schematic diagram (or diagrams) of all systems as installed,  including equipment and ancillary schedules. Show scheduled information on diagram.

B.     Identify all items by appropriate reference characters.

C.       Control Schematics

Supply and fix a referenced schematic diagram (or diagrams) of all control systems as installed, including equipment and ancillary schedules. Show scheduled information on diagram.

D.      Identify all items by appropriate reference characters.

E.      Location

F.       Fix in each boiler house, calorifier room, plant room or equipment room.

G.      Finish

H.     Hardboard 3mm thick set in hardwood frame and glazed with 1.5mm clear acrylic.

- System Identification Installation Charts, Plastic Encapsulated

A.      System Schematics

Supply and fix a referenced schematic diagram (or diagrams) of all systems as installed, including equipment and ancillary schedules. Show scheduled information on diagram. Identify all items by appropriate reference characters.

B.     Control Schematics

C.  Supply and fix a referenced schematic diagram (or diagrams) of all control systems as installed, including equipment and ancillary schedules. Show scheduled information on diagram. Identify all items by appropriate reference characters.

D.   Location

E.   Fix in each boiler house, calorifier room, plant room or equipment room.

F.  Finish

G.   Plastic encapsulated chart.

- Execution Miscellaneous

A.    Color not covered by this Specification must be agreed with the Consultant before work commences on site.

B.   Labels shall be permanently fixed using rivets or self tapping screws, sharp edges or tips of the screws, shall be removed.

C.    Control devices, shall be labeled by reference and function in accordance with circuit and layout diagrams.

D. Similar labels shall be affixed below each instrument on the instrument panel and shall indicate the purpose of the instrument and the respective boiler, tank or other appliance to which its recordings are applicable, and all relevant performance data as appropriate to the item of plant to enable easy identification at a later date.

E.  Cables shall be permanently designated using sleeves or ferrules at every termination in accordance with schematic wiring diagrams.

- All terminals shall be designated in accordance with circuit and layout diagrams. The designation of terminals may be achieved by the use of proprietary labels supplied as part of the product supplied by the terminal manufacturer.

G. All valves controlling mains and sub-circuits for all services shall be labeled before the works are commissioned in accordance with a schedule of valves, which shall correspond with valves indicated upon the final as-installed drawings and any circuit control diagrams considered necessary.

H. The Contractor shall supply to the Consultant details of the tagging system he intends to use together with a schedule of all valves and equipment with a dedicated tag number related to location, before installation of these items will be allowed to commence.

J .The schedules and schematic diagrams shall be framed and glazed and hung in the relevant plant rooms; an alternative method may be submitted to the Consultant for approval. Duplicate copies of the schedules and schematic diagrams shall be submitted to the Consultant for approval.

END OF SECTION