- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Electrical identification for communication systems in items for easy operation and maintenance including, but not limited to the following:

            - Nameplates and labels.

            - Wire markers.

            - Color coding of raceways.

            - Circuit identification charts.

            - Cable identification tags.

            - Cable warning tapes.

            - Equipment warning/danger signs.

      - REFERENCES

        - IEC 364 - Electrical Installations

        - BS 7671 - IEE Wiring Regulations, 17th Edition with all current additions and amendments.

        - IEC 391 - Marking of Insulated Conductors

        - IEC 445 - Equipment Terminals (Identification of Equipment Terminals and Terminations of Certain Designated Conductors).

        - IEC 446 - Identification of Bare Conductors by Colors or Numerals.

        - ISO/IEC 11801- 2nd Edition, Amend 2: 2010: Information technology - Generic cabling for        customer premises.

        - ISO/IEC 18010:2002, Information technology – Pathways and spaces for customer premises Cabling.

        - ISO/IEC TR 14763-3, Information technology – Implementation and operation of customer premises cabling – Part 3: Testing of optical fiber cabling.

        - ISO/IEC TR 14763-2, Information technology – Implementation and operation of customer premises cabling – Part 2: Planning and installation

        - Local Codes and requirements of Authorities/ Telecom services provider.

      - SUBMITTALS

        - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

        - Product Data:

          - Submit manufacturer’s catalog literature for each product required.

          - Submit electrical identification schedule including list of wording, symbols, letter size, color coding, tag number, location, and function.

        - Method statement for system’s component installation, testing and commissioning.

        - Samples:

          - Submit two tags, actual size.

          - Submit two labels, actual size.

          - Submit two samples of each type of identification products applicable to project.

          - Submit two nameplates, 100 x 100 mm in size illustrating materials and engraving quality.

          - It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Manufacturer's Installation Instructions: Indicate installation instructions, special procedures, and installation.

      - CLOSEOUT SUBMITTALS

        - Comply with requirements of Division 01.

        - Project Record Documents: Record actual locations of tagged devices; include tag numbers.

      - QUALIFICATIONS

        - Manufacturers: Firms regularly engaged in manufacture of items the types, sizes and ratings required, whose products have been in satisfactory use in similar service for not less than 5 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - QUALITY ASSURANCE

        - All items of communication Identification shall be comply with the requirements of BS and Local Standards Organization.

      - DELIVERY, STORAGE, AND HANDLING

        - Product Requirements for transporting, handling, storing, and protecting products.

        - Accept identification products on site in original containers. Inspect for damage.

        - Accept materials on site in original factory packaging, labeled with manufacturer's identification, including product density and thickness.

        - Protect insulation from weather and construction traffic, dirt, water, chemical, and mechanical damage, by storing in original wrapping.

      - ENVIRONMENTAL REQUIREMENTS

        - Comply with requirements of Division 01.

        - Install labels, nameplates only when ambient temperature and humidity conditions for adhesive are within range recommended by manufacturer.

      - SPARE PARTS

        - Supply as maintenance stock, additional labels and name plates of all types and sizes, amounting to one unit for every 10 installed units, but not less than two units of each type and size.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers.

- PRODUCTS

      - NAMEPLATES AND LABELS

        - Nameplates and labels shall be engraved on a three-layer 2 traffolyte plate having minimum thickness of 2 mm, securely screwed to the housing and have black letters on white background in Arabic and English.

        - The name plates and labels shall be required for each communication cabinets and devices/components.

        - Lettering shall be block capitals standing:

          - 6 mm high for identifying individual equipment and loads.

          - 10 mm high for identifying grouped equipment and loads.

        - Labels using embossed adhesive tape with 6mm white letters on black background or transparent adhesive tape with 6 mm black letters, as selected by the Engineer, shall be used for identification of individual low current outlets, speakers, junction/pull boxes, communication boxes and fittings, etc.

      - WIRE MARKERS

        - Wire markers shall be split sleeve or tubing type.

        - The wire markers shall be required for each conductor, pull boxes, outlets, junction boxes and each load connection.

        - All communication circuits and control circuits shall require wire markers.

      - COLOUR CODING OF RACEWAYS

        - Provide color bands with printed description of each system, minimum 75 mm wide for all cable trays/ladders and trunking runs. These color bands shall be applied at each electrical distribution/panel board, low current system control panels and junction box locations and at 15 m centers within an area.

        - Provide color bands with printed description of each system, minimum 25 mm wide for conduits up to 25 mm in diameter and one-half the conduit diameter for larger conduits, applied at panel and pull box locations, within each room, and at 6 m centers within an area.

        - Following color banding shall be used for the raceways of various communication systems, however subject to final decision of the Engineer. Color bands for the communication systems not described here shall be as agreed on site:

          - Fire alarm : red.

          - Telephone : blue.

          - Sound : yellow.

          - Data : purple.

          - Television : rust.

      - CIRCUIT IDENTIFICATION CHARTS

        - Individual circuit identification charts shall be provided for all communication cabinets, control s, etc. giving following information as a minimum.

          - Circuit numbers

          - Outgoing terminal numbers.

        - Charts shall be typed on A4 size sheets. They shall be enclosed in a clear plastic envelope and shall be securely fixed to the inside cover of the unit. Additional copies of the charts shall be included in the Operation and Maintenance Manuals.

      - CABLE IDENTIFICATION TAGS

        - All cables which exit from manholes, vaults, hand holes, shall be properly tagged or labeled. Tags shall be permanent, non-corrodible and clearly readable. Tags should include the information listed below for the various circuit categories:

          - Cable identification tags for communication wires and cables circuits shall be of an opaque nylon material arranged to include a marker plate, non-releasing nylon ties, and cable fastening tail. One side shall be roughened to hold black nylon permanent ink. Identification shall be permanent and waterproof. The holding device shall be designed to allow the fastening tail to pass around the cable through the holding device, and prevent removal of the tail without cutting it loose from the marker. Cable identification shall be inscribed in Arabic and English.

      - CABLE WARNING TAPES

        - For underground cables use warning tapes according to the standard practice of Authority and applicable international standards.

        - Cable warning tapes shall be of polythene, not less than 150 mm wide and at least 0.25 mm thick.

        - For buried low current/communication cables or duct banks, use warning tapes as per the standard practice of Local Telecom Supplier and applicable international standards.

      - LANGUAGE

        - The Arabic and English languages shall be used for all labeling and charts.

      - LABEL AND IDENTIFICATION

        - Each item of the communication Installation shall be fitted with a non-corrodible label/name plate clearly indicating its function giving at least the following information (Both in English and Arabic):

          - Manufacturer’s name.

          - Country of origin.

          - Type / model number or code.

          - Compliance mark of the international standard(s).

- EXECUTION

      - PREPARATION

        - Degrease and clean surfaces to receive adhesive for identification materials.

        - Prepare surfaces in accordance with Section 09 90 00 for stencil painting.

      - INSTALLATION

        - Install identifying devices after completion of painting.

        - Nameplate Installation:

          - Install nameplate parallel to equipment lines.

          - Install nameplate for each electrical distribution and control equipment enclosure with corrosive-resistant mechanical fasteners, or adhesive.

          - Install nameplates for each control panel and major control components located outside panel with corrosive-resistant mechanical fasteners, or adhesive.

          - Secure nameplate to equipment front using screws, rivets, or adhesive.

          - Secure nameplate to inside surface of door on recessed panels in finished locations.

        - Label Installation:

          - Install label parallel to equipment lines.

          - Install label for identification of individual control device stations.

          - Install labels for permanent adhesion and seal with clear lacquer.

        - Wire Marker Installation:

          - Install wire marker for each conductor at pull boxes, outlet and junction boxes, and each load connection.

          - Mark data cabling at each end. Install additional marking at accessible locations along the cable run.

          - Install labels at data outlets identifying patch panel and port designation as indicated on Drawings.

        - Stencil Installation:

          - Apply stencil painting in accordance with Section 09 90 00.

        - Underground Warning Tape Installation:

          - Install underground warning tape along length of each underground conduit, raceway, or cable (150 to 200 mm) below finished grade, directly above buried conduit, raceway, or cable.

- END OF SECTION