SECTION 23 0913

INSTRUMENTATION AND CONTROL DEVICES FOR HVAC

PART 1 GENERAL

- SECTION INCLUDES

- Thermostats.

- Humidistats.

- Control valves.

- Automatic dampers.

- Damper operators.

- Miscellaneous accessories.

- RELATED REQUIREMENTS

- REFERENCE STANDARDS

- AMCA 500-D - Laboratory Methods for Testing Dampers for Rating; Air Movement and Control Association International, Inc.; 2012.

- ASTM D1693 - Standard Test Method for Environmental Stress-Cracking of Ethylene Plastics; 2012.

- NEMA 250 - Enclosures for Electrical Equipment (1000 Volts Maximum); National Electrical Manufacturers Association; 2014.

- NEMA DC 3 - Residential Controls - Electrical Wall-Mounted Room Thermostats; National Electrical Manufacturers Association; 2013.

- NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilation Systems; National Fire Protection Association; 2012.

- ADMINISTRATIVE REQUIREMENTS

- Preinstallation Meeting: Conduct a preinstallation meeting one week before starting work of this section; require attendance by all affected installers.

- Sequencing: Ensure that utility connections are achieved in an orderly and expeditious manner.

- SUBMITTALS

- Product Data: Provide description and engineering data for each control system component. Include sizing as requested. Provide data for each system component and software module.

- Shop Drawings: Indicate complete operating data, system drawings, wiring diagrams, and written detailed operational description of sequences. Submit schedule of valves indicating size, flow, and pressure drop for each valve. For automatic dampers indicate arrangement, velocities, and static pressure drops for each system.

- Samples: Submit two of each type of room thermostat and cover.

- Design Data: Provide design data for sizing and selection of compressor.

- Manufacturer's Instructions: Provide for all manufactured components.

- Operation and Maintenance Data: Include inspection period, cleaning methods, recommended cleaning materials, and calibration tolerances.

- Project Record Documents: Record actual locations of control components, including panels, thermostats, and sensors. Accurately record actual location of control components, including panels, thermostats, and sensors.

- Revise shop drawings to reflect actual installation and operating sequences.

- Warranty: Submit manufacturers warranty and ensure forms have been filled out in Employer/Owner s name and registered with manufacturer.

- QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in manufacturing the Products specified in this section with minimum ten years documented experience.

- Installer Qualifications: Company specializing in performing the work of this section with minimum five years experience approved by manufacturer.

- Products Requiring Electrical Connection: Listed and classified by Underwriters Laboratories Inc., as suitable for the purpose specified and indicated.

- WARRANTY

- See Section 01 7800 - Closeout Submittals, for additional warranty requirements.

- Provide five year manufacturer's warranty for control air compressors.

PART 2 PRODUCTS

- EQUIPMENT - GENERAL

- Products Requiring Electrical Connection: Listed and classified by Underwriters Laboratories Inc., as suitable for the purpose specified and indicated.

- CONTROL PANELS, SWITCHES AND ELECTRICAL ISOLATORS

- Unitized cabinet type for each system under automatic control with relays and controls mounted in cabinet and temperature indicators, pressure gages, pilot lights, push buttons and switches flush on cabinet panel face.

- NEMA 250, general purpose utility enclosures with enameled finished face panel.

- Or IP Code, International Protection Marking, IEC standard 60529.

- Provide common keying for all panels.

- Indoor panels shall be either NEMA 250 type 2 or IP 54.

- Outoor panels shall be either NEMA 250 type 6 or IP 65.

- Each composite panel shall include a main isolator interlocked with the door that shall be lockable. All panels shall be finished with stove enamel internally and externally. All panels shall be sealed against ingress of moisture, dust and vermin. All starters and controls shall be located in panels unless agreed otherwise by the Engineer.

- An earthing bar shall be provided throughout the entire length of the control panel.

- A minimum of 2 doors shall be provided on any panels wider than 800 mm that shall be fabricated to form rigid trays with dust excluding gaskets around their perimeter, doors shall be filled with hinges to facilitate the removal of the door panels if required, all doors shall be interlocked or arranged such that the door that provides access to the main isolator must be opened first. all door locks shall be provided with common keys.

- Control switches shall comply with BS EN 60947-5-1.

- Switches shall be of the rotary type.

- All control switches shall be capable of being locked in the "off" position, unless stated otherwise.

- The contacts of all switches shall be strong and have a positive wiping action when operated.

- All control switches shall be provided with labels.

- All control panels shall be provided with a defeat proof door interlock isolator controlling the main incoming supply. The isolator shall be capable of making and breaking on full load without damage. Additionally the isolator shall have:-

- Auxiliary contacts to isolate any secondary supplies to the control panel.

- Manual override switch to enable the control system only to be energised whilst the incoming supplies are isolated.

- All terminals of the isolator (incoming and outgoing) are to be shrouded to prevent accidental contact.

- The panel shall be constructed such that power (3 phase and single phase) equipment is located behind the interlocked isolator door.

- Control (extra low voltage) equipment shall be located behind the second or subsequent doors to ensure segregation from power equipment.

- The control system operating voltage shall not exceed 230V without prior authorization.

- All internal wiring shall be enclosed within wireways. Inter wiring that is required to pass between the power and control sections of the panel shall be enclosed within separate or segregated wire ways to ensure electrical separation of the power and control systems.

  - DAMPERS

- Performance: Test in accordance with AMCA 500-D.

- Frames: Galvanized steel, welded or riveted with corner reinforcement, minimum 2.66 mm (12 gage, 0.1046 inch).

- Blades: Galvanized steel, maximum blade size 200 mm (8 inches) wide, 1200 mm (48 inches) long, minimum 0.76 mm (22 gage, 0.0299 inch), attached to minimum 13 mm (1/2 inch) shafts with set screws.

- Blade Seals: Synthetic elastomeric inflatable mechanically attached, field replaceable.

- Jamb Seals: Spring stainless steel.

- Shaft Bearings: Oil impregnated sintered bronze.

- Linkage Bearings: Oil impregnated sintered bronze.

- Leakage: Less than one percent based on approach velocity of 10 m/sec (2000 ft/min) and 1.0 kPa (4 inches wg).

- Maximum Pressure Differential: 1.5 kPa (6 inches wg).

- Temperature Limits: -40 to 93 degrees C (-40 to 200 degrees F).

  - DAMPER OPERATORS

- General: Provide smooth proportional control with sufficient power for air velocities 20 percent greater than maximum design velocity and to provide tight seal against maximum system pressures. Provide spring return for two position control and for fail safe operation.

- Provide sufficient number of operators to achieve unrestricted movement throughout damper range.

- Provide one operator for maximum 3.34 sq m (36 sq ft) damper section.

- Pilot Positioners: Starting point adjustable from 15 to 83 kPa (2 to 12 psig) and operating span adjustable from 35 to 90 kPa (5 to 13 psig).

- Electric Operators:

- Spring return, adjustable stroke motor having oil immersed gear train, with auxiliary end switch.

- Inlet Vane Operators:

- High pressure with pilot positioners and sufficient force to move vanes when fan is started with vanes in closed position. Return vane operator to closed position on fan shutdown.

  - INPUT/OUTPUT SENSORS

- Temperature Sensors:

- Use RTD type temperature sensing elements with characteristics resistant to moisture, vibration, and other conditions consistent with the application without affecting accuracy and life expectancy.

- Construct RTD of nickel or platinum with base resistance of 1000 ohms at 26 degrees C (70 degrees F).

- 100 ohm platinum RTD is acceptable if used with project DDC controllers.

- Temperature sensing device must be compatible with project DDC controllers.

- Performance Characteristics:

- RTD:

- Room Sensor Accuracy: Plus/minus 0.28 degrees C (0.50 degrees F) minimum.

- Duct Averaging Accuracy: Plus/minus 0.28 degrees C (0.5 degrees F) minimum.

- Chilled Water Accuracy: Plus/minus 0.28 degrees C (0.5 degrees F) minimum.

- All Other Accuracy: Plus/minus 0.36 degrees C (0.65 degrees F) minimum.

- Range: Minus 40 degrees C (Minus 40 degrees F) through 104.4 degrees C (220 degrees F) minimum.

- Temperature Transmitter:

- Accuracy: [0.3] degrees C ([0.54] degrees F) minimum.

- Output: 4 - 20 mA or 0-10 VDC.

- Sensing Range:

- Provide limited range sensors if required to sense the range expected for a respective point.

- Use RTD type sensors for extended ranges beyond minus 34.4 degrees (minus 30 degrees F) to 114.4 degrees C (230 degrees F).

- Use temperature transmitters in conjunction with RTD's when RTD's are incompatible with DDC controller direct temperature input.

- Wire Resistance:

- Use appropriate wire size to limit temperature offset due to wire resistance to

- 56 degrees C (1.0 degree F) or use temperature transmitter when offset is greater than 0.56 degrees C (1.0 degree F) due to wire resistance.

- Compensate for wire resistance in software input definition when feature is available in the DDC controller.

- Room Sensors: Locking cover.

- Outside Air Sensors: Watertight inlet fitting shielded from direct rays of the sun.

- Immersion Temperature Sensors: A sensor encased in a corrosion-resistant probe with a threaded-enclosure service entry body.

- Ceiling and Recessed Mount Temperature Senors: Ceiling-mounted sensor in a low-profile housing.

- Room Security Sensors: Stainless steel cover plate with insulated back and security screws.

- Room Temperature Sensors with Integral Digital Display (for AHU control or room temperature monitoring):

- Construct for surface or wall box.

- Provide a five button keypad with the following capabilities:

- Indication of space and outdoor temperatures.

- Setpoint adjustment to accommodate room setpoint, DDC Input/Output Points List, and Sequence of Operation.

- Controller mode status (cooling or heating).

- Password enabled setpoint and override modes, if available.

- Temperature Averaging Elements:

- Use on duct sensors for ductwork 0.93 sq m (10 sq ft) or larger.

- Use averaging elements where prone to stratification with sensor length 2.5 m (8 ft), or 5 m (16 ft).

- Provide for all mixed air and heating coil discharge sensors regardless of duct size.

- Insertion Elements:

- Use in ducts not affected by temperature stratification or smaller than 1 sq m (11 sq inches).

- Provide dry type, insertion elements for liquids, installed in immersion wells, with minimum insertion length of 60 mm (2.5 inches).

- Damper Position Indication: Potentiometer mounted in enclosure with adjustable crank arm assembly connected to damper to transmit 0 - 100 percent damper travel.

  - THERMOSTATS

- Electric Room Thermostats:

- Type: NEMA DC 3, 24 volts, with setback/setup temperature control.

- Service: Cooling and heating.

- Covers: Locking with set point adjustment, with thermometer.

- Line Voltage Thermostats:

- Integral manual On/Off/Auto selector switch, single or two pole as required.

- Dead band: Maximum one degree C (2 degrees F).

- Cover: Locking with set point adjustment, with thermometer.

- Rating: Motor load.

- Room Thermostat Accessories:

1. Thermostat Covers: Brushed aluminum.

- Insulating Bases: For thermostats located on exterior walls.

- Thermostat Guards: Metal mounted on separate base.

- Adjusting Key: As required for device.

- Aspirating Boxes: In front entrances and public access areas for thermostats requiring flush installation.

- Outdoor Reset Thermostat:

- Remote bulb or bimetal rod and tube type, proportioning action with adjustable throttling range, adjustable setpoint.

- Scale range: 2 to 35 degrees C (-10 to 70 degrees F).

- Immersion Thermostat:

1. Remote bulb or bimetallic rod and tube type, proportional action with adjustable setpoint and adjustable throttling range.

- Airstream Thermostats:

- Remote bulb or bimetallic rod and tube type, proportional action with adjustable setpoint in middle of range and adjustable throttling range.

- Averaging service remote bulb element: 2.3 m (7.5 feet).

- Electric Low Limit Duct Thermostat:

- Snap acting, single pole, single throw, manual reset switch that trips if temperature sensed across any 300 mm (12 inches) of bulb length is equal to or below setpoint,

- Bulb length: Minimum 6 m (20 feet).

- Provide one thermostat for every 1.86 sq m (20 sq ft) of coil surface.

- Electric High Limit Duct Thermostat:

- Snap acting, single pole, single throw, manual reset switch that trips if temperature sensed across any 300 mm (12 inches) of bulb length is equal to or above setpoint,

- Bulb length: Minimum 6 m (20 feet).

- Provide one thermostat for every 1.86 sq m (20 sq ft) of coil surface.

- Fire Thermostats:

- UL labeled, factory set in accordance with NFPA 90A.

- Normally closed contacts, manual reset.

PART 3 EXECUTION

- EXAMINATION

- Verify existing conditions before starting work.

- Verify that systems are ready to receive work.

- Beginning of installation means installer accepts existing conditions.

- Sequence work to ensure installation of components is complementary to installation of similar components in other systems.

- Coordinate installation of system components with installation of mechanical systems equipment such as air handling units and air terminal units.

- Ensure installation of components is complementary to installation of similar components.

- Coordinate installation of system components with installation of mechanical systems equipment such as air handling units and air terminal units.

- INSTALLATION

- Install in accordance with manufacturer's instructions.

- Check and verify location of thermostats with plans and room details before installation. Locate 1500 mm (60 inches) above floor. Align with lighting switches and humidistats. Refer to Section 26 2726.

- Mount freeze protection thermostats using flanges and element holders.

- Mount outdoor reset thermostats and outdoor sensors indoors, with sensing elements outdoors with sun shield.

- Provide separable sockets for liquids and flanges for air bulb elements.

- Provide thermostats in aspirating boxes in front entrances and public access areas.

- Provide guards on thermostats in entrances and public areas.

- Provide valves with position indicators and with pilot positioners where sequenced with other controls.

- Provide separate steam valves for each bank of coils. Provide two valves in parallel where steam load exceeds 0.10 kg/s (1500 lb/hr) with 1/3 - 2/3 load capacities sequenced with smaller valve opening first.

- Provide mixing dampers of opposed blade construction arranged to mix streams. Provide pilot positioners on mixed air damper motors. Provide separate minimum outside air damper section adjacent to return air dampers with separate damper motor.

- Provide isolation (two position) dampers of parallel blade construction.

- Provide pilot positioners on pneumatic damper operators sequenced with other controls.

- Install damper motors on outside of duct in warm areas. Do not install motors in locations at outdoor temperatures.

- Mount control panels adjacent to associated equipment on vibration free walls or free standing angle iron supports. One cabinet may accommodate more than one system in same equipment room. Provide engraved plastic nameplates for instruments and controls inside cabinet and engraved plastic nameplates on cabinet face.

- Install "hand/off/auto" selector switches to override automatic interlock controls when switch is in "hand" position.

- Provide conduit and electrical wiring in accordance with Section 26 2717. Electrical material and installation shall be in accordance with appropriate requirements of Division 26.

- MAINTENANCE

A. See Section 01 7000 - Execution and Closeout Requirements, for additional requirements relating to maintenance service.

END OF SECTION