SECTION 21 26 00

CLEAN-AGENT & AUTOMATIC FIRE SUPPRESSION SYSTEMS (FM-200)

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This section includes clean-agent and automatic fire suppression systems:

          - FM-200 automatic fire suppression systems

          - Accessories

      - REFERENCES

        - The system shall be designed and installed in accordance with the following standards:

        - Local civil defense code.

        - National Fire Protection Association (NFPA).

          - NFPA 13 – Installation of Sprinkler Systems.

          - NFPA 14 – Standpipes and Hose System.

          - NFPA 20 – Stationary Pumps for Fire Protection.

          - NFPA 24 – Private Fire Service Mains and Their Appurtenances.

          - NFPA 25 - Inspection, Testing & Maintenance of Fire Protection Systems.

          - NFPA 72 – 1996, National Fire Alarm Code.

        - Underwriters Laboratories, Inc. (UL).

        - American Society for Testing and Materials.

          - ASTM A 795, Specification for Black and Hot-Dipped Zinc-Coated (Galvanized) Welded and Seamless Steel Pipe for Fire Protection Use.

          - ASTM B 88, Specification for Seamless Copper Water Tube.

          - ASTM F 593, Stainless Steel Bolts, Hex Cap Screws, and Studs.

          - ASTM F 594, Stainless Steel Nuts

        - American Welding Society.

          - AWS A5.8, Specifications for Brazing Filler Metal.

        - Factory Mutual Engineering Corporation (FM).

      - DEFINITIONS

        - ATS:  Acceptance Testing Specifications.

        - EPO:  Emergency Power Off.

      - SYSTEM DESCRIPTION

        - Clean agent fire extinguishing system shall be engineered system for total flooding of the hazard area including the room cavity below the ceiling and below the raised floor (where provided). If smoke is detected in any zone, clean agent shall be discharged in all zones.

      - PERFORMANCE REQUIREMENTS

        - Design clean-agent extinguishing system and obtain approval from authorities having jurisdiction. Design system for Class A, B, or C fires as appropriate for areas being protected and include safety factor. Use clean agent indicated and in concentration suitable for normally occupied areas. Protected areas shall include any shafts or enclosures opening into the protected area.

        - Performance Requirements:  Discharge HFC 227ea within 10 seconds and maintain concentration by volume at 70 deg F (21 deg C) for 10-minute holding time in hazard areas.

- Discharge CO2 within 1 minute for surface fires and 7 minutes for deep-seated fires (Dry Chemical). But the rate shall not be high than that required to develop a concentration of 30% by volume in two minutes.

          - HFC 227 ea: 7.1 percent.

          - IG 541 		: 38 percent.

- C.	Design Concentration: CO2

          - 34% by volume for surface fire.

          - 50% by volume for deep seated fires – Dry Electrical.

- D.	Minimum Working Pressures:

- 1.	System Capabilities:  Minimum 620-psig (4278-kPa) calculated working pressure and 360-psig (2484-kPa) initial charging pressure.

- 2.	IG-541: 2575 psig (17.76 MPA) calculated working and initial charging for tanks and manifold. 1000 psig (6900 KPA) for piping downstream of the pressure-reducing orifice

- E.	Automatic System Operating Sequence:  As follows:

- 1.	Actuating First Detector:  Visual indication on annunciator panel, energize audible alarm and visual alarms (slow pulse), shut down air-conditioning and ventilating systems serving protected area, close doors in protected area, and send signal to fire alarm system.

- 2.	Actuating Second Detector: Visual indication on annunciator panel, energize audible and visual alarms (fast pulse), shut down power to protected equipment, start time delay for extinguishing-agent discharge for 30 seconds, and discharge extinguishing agent. Send signal to fire alarm system.

- 3.	Extinguishing-agent discharge will operate audible alarms and strobe lights inside and outside the protected area.

- F.	Manual stations shall immediately discharge extinguishing agent when activated.

- G.	Operating abort switches will delay extinguishing-agent discharge as long as it is depressed while being activated, and switches must be reset to prevent agent discharge.  Release of hand pressure on the switch will cause agent discharge if the time delay has expired.

- H.	Emergency Power Off:  Will terminate power to equipment in the protected space immediately on actuation.

- J.	Low-Agent Pressure Switch:  Initiate trouble alarm if sensing less than set pressure.

- K.	Power Transfer Switch:  Transfer from normal to stand-by power source.

      - SUBMITTALS

        - Product Data:  For the following:

          - Extinguishing-agent containers.

          - Extinguishing agent.

          - Discharge nozzles.

          - Control panels.

          - Detection devices.

          - Manual stations.

          - Switches.

          - Alarm devices.

          - Pipe hangers and supports including seismic restraints.

        - Shop Drawings:  Signed and sealed by a qualified professional engineer.  Include design calculations.

        - Permit Approved Drawings:  Working plans, prepared according to NFPA 2001.

        - Maintenance Data:  For components to include in maintenance manuals.

      - QUALITY ASSURANCE

        - FMG approved and NRTL listed components.

        - Quality standards: NFPA 2001 and UL1058

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - Enclosure and Integrity Test (FM-200): Carried out according to the latest edition of NFPA 2001.

      - EXTRA MATERIALS

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.  Deliver extra materials to Owner.

          - Detection Devices: Not less than 20 percent of amount of each type installed.

          - Container Valves: Not less than 10 percent of amount of each size and type installed.

          - Nozzles:  Not less than 20 percent of amount of each type installed.

          - Each clean agent system shall include main and reserve bank of agent cylinders.

      - WARRANTY

- Furnish two-year manufacturer warranty.

- PRODUCTS

      - STANDARD PRODUCTS

        - Materials and equipment shall be standard products of a manufacturer regularly engaged in the manufacture of such products and shall essentially duplicate items that have been in satisfactory use for at least 2 years prior to bid opening.

      - FM-200 AUTOMATIC FIRE SUPPRESSION SYSTEMS

- A.	GENERAL

- Clean agent system shall be provided for the protection of the areas as shown on the drawings.

- The system layouts and components shall be as shown on the Contract drawings and as specified hereafter.

The system shall comprise the following:

- Cylinder and valve assembly

- Cylinder actuating controls

- Cylinder pressure supervisory switch

- Pressure switch

- Pressure trip & fire curtains (if required)

- Nozzles

- Pipework, tubing and fittings

- Detection, actuation and control system

- All wiring, conduits and accessories

The work shall also include all provisions required to put the system in good operating conditions

- B.	PIPING MATERIALS

- 1.	Refer to Part 3 piping applications Article retained for applications of pipe, tube, fitting, and joining materials.

- 2.	Piping, Valves, and Discharge Nozzles:  Comply with types and standards listed in NFPA 2001, Section "Distribution," for charging pressure of system.

- C.	PIPE AND FITTINGS

- 1.	Steel Pipe: ASTM A 53/A 53M, Type S, Grade B or ASTM A 106, Grade B; Schedule 40, galvanized seamless steel pipe.

- -	Threaded Fittings (DN 50) and smaller:

            - Malleable-Iron Fittings:  ASME B16.3, Class 300.

- Forged-Steel Welding Fittings:  ASME B16.11, Class 3000, socket pattern.

- -	Grooved-End Fittings:  FMG approved and NRTL listed, ASTM A 47/A 47M malleable iron or ASTM A 536 ductile iron, with dimensions matching steel pipe and ends factory grooved according to AWWA C606.

- D.	VALVES

- 1.	General:  Brass; suitable for intended operation.

- 2.	Container Valves:  With rupture disc or solenoid and manual-release lever, capable of immediate and total agent discharge and suitable for intended flow capacity.

          - Valves in Sections of Closed Piping and Manifolds:  Fabricate to prevent entrapment of liquid, or install valve and separate pressure relief device.

          - Valves in Manifolds:  Check valve; installed to prevent loss of extinguishing agent when container is removed from manifold.

- E.	EXTINGUISHING-AGENT CONTAINERS (CYLINDERS)

- 1.	Description: Steel tanks complying with ASME Boiler and Pressure Vessel Code:  Section VIII, for unfired pressure vessels. Containers first fill shall be factory filled.

- -	Finish:  Red, enamel or epoxy paint.

- -	Manifold: Fabricate with valves, pressure switches, selector switch, and manifold connections for main- and reserve-supply banks of multiple storage containers.

- -	Storage-Tank Brackets:  Factory- or field-fabricated retaining brackets consisting of steel straps and channels; suitable for container support, maintenance, and tank refilling or replacement.

- -	For large cylinders that are difficult to be weighed a level indicator shall be provided.

- -	Cylinder Valve: shall be of high flow rate design to provide the rapid discharge time.

- The valve shall be of the pressure seated type and has a brass, brass body, brass piston with seal, a pressure-releasing pilot check assembly for manual actuation, a safety disk assembly and a pressure gauge.

- The valve shall be equipped with hand lever, and pull out locking pin for local manual mechanical control.

- The cylinder valve shall have a connection port with built-in check valve for the connection of electric solenoid valve for electric actuation.

        - CYLINDER ACTUATING CONTROLS

          - Local Manual Mechanical Control

- The cylinder valve is actuated by moving the actuator lever through 90 degree, which causes the pin to depress and open the pilot check on the cylinder valve. This action releases the pressure above the piston allowing the cylinder valve to open fully, and permitting agent to discharge through the outlet.

- The locking pin shall be inserted in the control lever and body and secured with lead seal and wire to maintain the lever in the set position.

- The lever shall be marked with arrow and the word "SET".

          - Electric Solenoid

- The solenoid valve shall be normally closed and shall open when electric energy is applied, thus relieving the pressure above the cylinder valve piston causing the cylinder valve to open and permitting agent to discharge through the outlet.

- The solenoid valve shall be fitted a swivel nut for mechanical connection and removal from the cylinder valve.

- The solenoid valve shall be furnished with minimum 60 cm wire leads and ½" diameter conduit connection for electrical connection to the detection release.

          - Cylinder Pressure Supervisory Switch

- This switch shall be used to provide a trouble signal if the pressure in the cylinder drops to approximately 220 psig.

- The cylinder pressure supervisory switch shall be furnished as assembly with solenoid valve and swivel nut conductor.

- The switch wiring shall not be connected to the solenoid operating circuit.

          - Pressure Switch

- The pressure switch shall be used to perform interlock functions, sounding alarms and shutting down electrical motors of fans used for ventilation and air conditioning system in the protected areas.

- The pressure switch shall be actuated only by the pressure of the extinguishing when discharged through the piping system, upon actual system discharge.

- The connection between the discharge piping and the pressure switch shall be made with ¼" O.D. copper tubing and flared tubing fittings including reducing coupling, nipple and union for pressure switch connection, limitation of thing length shall be as recommended by the manufacturer.

- The pressure switch shall have ½" male pipe thread and reset.

- The pressure switch shall be furnished with fire leads and ½" diameter conduit connection for electrical connection to be alarm circuit and electrical fan motors.

- The wire leads shall lead through 3/8" flexible steel conduit using suitable connectors at the pressure switch and at the junction box.

          - Pressure Trip

- The pressure trip shall be used to release dampers or other weight or spring-operated devices, such as fire curtains, which are normally open.

- The pressure trip shall be actuated only by the pressure of the extinguishing when discharged through the piping system, upon actual system discharge.

- The pressure trip shall be furnished with vents S-hook, stainless steel cable to be released, cable clamp, clearance holes, and mounting bolts or lag screws.

- Limitation of the tubing length shall be as recommended by the manufacturer.

- Automatic fire curtains shall be provided for each opening and louver where located in the protected area walls.

- The fire curtains shall be spring operated type maintained at normally open position and must be closed to seal the protected area enclosure to prevent the scope or dilution of the Agent extinguishing when discharged through piping system.

- G.	FIRE-EXTINGUISHING CLEAN AGENT

- 1.	Clean Agent:  HFC 227ea, heptafluoropropane, FM-200.

- H.	DISCHARGE NOZZLES

- 1.	Equipment manufacturer's standard corrosion-resistant material, one-piece brass or aluminum alloy of type, discharge pattern, and capacity required for application.

- I.	MANIFOLD AND ORIFICE UNIONS

- 1.	Description:  NRTL-listed device with minimum 2175-psig (15-MPa) pressure rating, to control flow and reduce pressure of IG-541 gas in piping.

- -	NPS 2 (DN 50) and Smaller:  Piping assembly with orifice, sized for system design requirements.

- 2.	NPS 2-1/2 (DN 65) and Larger:  Piping assembly with nipple, sized for system design requirements.

- J.	CONTROL PANELS

- 1.	Description:  FMG approved or NRTL listed, including equipment and features required for testing, supervising, and operating fire-extinguishing system.

- 2.	Power Requirements:  240-V ac; with electrical contacts for connection to system components and fire alarm system, and transformer or rectifier as needed to produce power at voltage required for accessories and alarm devices.

- 3.	Enclosure:  NEMA ICS 6, Type 1, enameled-steel cabinet.

- -	Mounting:  Recessed flush.

- 4.	Supervised Circuits:  Separate circuits for each independent hazard area.

- -	Detection circuits equal to the required number of zones, or addressable devices assigned to the required number of zones.

- -	Manual pull-station circuit.

- -	Alarm circuit.

- -	Release circuit.

- -	Abort circuit.

- -	EPO circuit.

- 5.	Provide the following control-panel features:

- -	Electrical contacts for shutting down fans, activating dampers, and operating system electrical devices.

- -	Automatic switchover to standby power at loss of primary power.

- -	Storage container, low-pressure indicator.

- -	Service disconnect to interrupt system operation for maintenance with visual status indication on the annunciator panel.

          - Annunciator Panel:  Graphic type showing protected, hazard-area plans and locations of detectors, abort, EPO, and manual stations. Include lamps to indicate device-initiating alarm, electrical contacts for connection to control panel, and stainless-steel or aluminum enclosure.

          - Standby Power: Lead-acid or nickel-cadmium batteries with capacity to operate system for 72 hours and alarm for minimum of 15 minutes. Include automatic battery charger, with varying charging rate between trickle and high depending on battery voltage that is capable of maintaining batteries fully charged. Include manual voltage control, dc voltmeter, dc ammeter, electrical contacts for connection to control panel, and suitable enclosure.

- K.	DETECTION DEVICES

The detection and control system shall employ photoelectric, ionization smoke detectors and heat detectors. A single detector activated shall cause an alarm signal to be generated.   A second detector activated shall generate a pre-discharge signal and start the pre-discharge conditions.

- Ionization Smoke Detectors: The products of combustion detectors, ionization type, shall utilize solid state circuitry and be of the dual chamber, bipolar configuration.  One chamber shall be opened to sense particles of combustion while the other will be used as a reference chamber for stability.  The unit shall be designed so as to be unaffected by FR and energy from 1 kHz through 1000 MHz in a field strength of up to 10 m-volts per meter. Ionization detectors which are designed such that sensitivity decreases in the presence of air movement shall not be permitted.  The detectors shall also be unaffected by air velocities up to 1000 FPM.

- Photoelectric Smoke Detectors: The products of combustion detectors, photoelectric type, shall utilize solid state circuitry, a pulsed, infrared, L.E.D. light source and a silicon photo diode receiving element.  The receiving element will normally not sense any light from the L.E.D source.  When smoke particles enter the sensing chamber, the light source shall be reflected to the sensing element.  Comparator circuitry shall be used so as to discriminate between a valid “fire” signal and an intermittent “non-fire” source.  The entrance to the sensing chamber shall be surrounded by a fine stainless steel mesh so as to prevent ready entry by insects, lint or dust.  Unit shall be dew-proof and uninfluenced by high air velocity.

The detectors shall be Factory Mutual Approved and UL listed to meet UL Standard 268.

- Thermal Detector: The thermal detector shall be a rate-compensated fixed temperature type.  The fixed temperature setting shall be in accordance with NFPA 72E recommendations.

4.	Detection System for Fuel Rooms: The detection and control system shall employ photoelectric ionization smoke detectors and heat detectors. A single detector activated shall cause an alarm signal to be generated. A second detector activated shall generate a pre-discharge signal and start the pre-discharge conditions.

-	Optical Smoke detectors: shall be installed in all areas where required either by the appropriate NFPA standard or the authorizing having jurisdiction.

-	Flame Detectors: Radiant energy fire detection that is intended to detect flames and is designed to operate in dark normally lit environment where sunlight or other ambient lighting is assumed.

5.	Detection System Generators Room: The detection and control system shall employ two rate of rise heat detectors so that is a single detector is activated it shall activate an alarm signal, and when the second detector is activated it shall generate a pre-discharge signal and shall start the pre-discharge conditions.

6.	Detection System in Electrical Rooms: As described for generator room but with two optical smoke detectors.

- L.	MANUAL RELEASE STATIONS

- 1.	General Description: Surface FMG approved or NRTL listed, with clear plastic hinged cover, 120-V ac or low voltage compatible with controls.  Include contacts for connection to control panel. A protective cover that releases an alarm when opened shall be added to prevent inadvertent discharge.

- 2.	Manual Release: "MANUAL RELEASE" caption, and red finish. Unit can manually discharge extinguishing agent with operating device that remains engaged until unlocked.

- 3.	Abort Switch:  "ABORT" caption, momentary contact, with green finish.

- 4.	EPO Switch:  "EPO" caption, with yellow finish.

- M.	ALARM DEVICES

- 1.	Description:  FMG approved or NRTL listed, low voltage, and surface mounting, unless otherwise indicated.

- 2.	Bells:  Minimum 6-inch (150-mm) diameter.

- 3.	Horns:  90 to 94 dBA.

- 4.	Strobe Lights:  Translucent lens, with "FIRE" or similar caption.

      - SEALING OF OPENINGS

- A.	Openings shall be sealed in accordance with NFPA 12, NFPA 2001 & Civil Defense regulations.

- B.	Fire curtains or motorized smoke dampers shall be supplied to close openings and louvers to prevent escape of FM200.

- B.	Fire curtains shall be roll up type, made from fibre glass.

- C.	Curtains shall be installed in such a manner that upon receiving a signal from the control panel and before release of the FM200 gas, the holding mechanism will release the curtain to drop through a ‘U’ channel guide.

- D.	Motorized smoke dampers shall be according to section 23 33 00.

      - ELECTRICAL POWER AND WIRING

- A.	Electrical power, wiring, and devices are specified in Division 26 & 28.

      - ACCESSORIES

- A.	Weigh scales: for weighing agent cylinders in place without disconnecting them from the cylinder manifold for ease in maintenance.

- B.	Warning Nameplates as per NFPA 12 & NFPA 2001.

- EXECUTION

      - EXAMINATION

        - Examine areas and conditions, for compliance with hazard-area leakage requirements, installation tolerances, and other conditions affecting work performance.

      - PIPING APPLICATIONS

        - Piping Applications for 360 psig (2484-KPA) Charging pressure:

- 1.	NPS 2 (DN 50) and Smaller:  Schedule 40, steel pipe; malleable-iron threaded fittings; and threaded joints.

- 2.		NPS 2-1/2 and NPS 3 (DN 65 and DN 80):  Schedule 40, steel pipe; steel, grooved-end fittings; steel, keyed couplings; and grooved joints.

- 3.		NPS 4 (DN 100) and Larger:  Schedule 40, steel pipe; steel, grooved-end fittings; steel, keyed couplings; and grooved joints.

        - Piping Applications for 2175 psig (15-MPA) Charging Pressure:

          - Steel pipe: Schedule 80 with welded fittings for all sizes.

      - PIPING INSTALLATION

        - Install piping and other components level and plumb and according to manufacturers' written instructions.

        - Refer to Division 15 Section "Basic Mechanical Materials and Methods" for basic pipe installation and joint construction.

        - Grooved Piping Joints: Groove pipe ends according to AWWA C606 dimensions.  Assemble grooved-end steel pipe and steel, grooved-end fittings with steel, keyed couplings and lubricant according to manufacturer's written instructions.

        - Install extinguishing-agent containers anchored to substrate.

        - Install pipe and fittings, valves, and discharge nozzles according to requirements listed in NFPA 2001, Section "Distribution," and in ASME B31.1.

          - Install valves designed to prevent entrapment of liquid or install pressure relief devices in valved sections of piping systems.

          - Support piping using supports and methods according to NFPA 13 and Division 15 Section "Hangers and Supports."

          - Install control panels, detection system components, alarms, and accessories, complying with requirements of NFPA 2001, Section "Detection, Actuation, and Control Systems," as required for supervised system application.

      - CONNECTIONS

        - Drawings indicate general arrangement of piping, fittings, and specialties.

        - Install piping adjacent to extinguishing-agent containers to allow service and maintenance.

        - Connect electrical devices to control panel and to building's fire alarm system.  Electrical power, wiring, and devices are specified in Division 28 Section "Fire Alarm." From csi.

      - LABELING

        - Install labeling on piping, extinguishing-agent containers, other equipment, and panels according to NFPA 2001.

        - Install signs at entry doors for protected areas to warn occupants that they are entering a room protected with a clean-agent fire extinguishing system.

        - Install signs at entry doors to advise persons outside the room the meaning of the horn(s), bell(s), and strobe light(s) outside the protected space.

      - FIELD QUALITY CONTROL

        - Comply with operating instructions and procedures of NFPA 2001, Section "Approval of Installations."  Include the following tests and inspections to demonstrate compliance with requirements:

          - Check mechanical items.

          - Inspect extinguishing-agent containers and extinguishing agent, and check mountings for adequate anchoring to substrate.

          - Check electrical systems.

          - Check enclosure integrity. Comply with NFPA 2001, Section "Enclosure Inspection," and Appendix C, "Enclosure Integrity Procedure."

          - Perform functional pre-discharge test.

          - Perform system functional operational test including, EPO, abort, and manual release.

          - Check remote monitoring operations.

          - Check control-panel primary power source.

          - Perform "puff" test on piping system, using nitrogen.

        - Perform field-acceptance tests of each clean-agent extinguishing system when installation is complete.  Perform system testing only after hazard-area enclosure construction has been completed and openings sealed.  Comply with operating instructions and procedures of NFPA 2001, Section "Approval of Installations."  Include the following to demonstrate compliance with requirements:

          - Perform functional predischarge test.

          - Perform system functional operational test.

          - Check remote monitoring operations.

          - Check control-panel primary power source.

          - Perform "puff" test on piping system, using nitrogen.

        - Correct malfunctioning equipment, then retest to demonstrate compliance. Replace equipment that cannot be corrected or does not perform as specified and indicated, then retest to demonstrate compliance. Repeat procedure until satisfactory results are obtained.

          - Report test results promptly and in writing to The Engineer and authorities having jurisdiction.

        - Perform the following field tests and inspections and prepare test reports:

          - After installing clean-agent extinguishing piping system and after electrical circuitry has been energized, test for compliance with requirements.

          - Perform each electrical test and visual and mechanical inspection stated in NETA ATS, Sections "Inspection and Test Procedures" and "System Function Tests."  Certify compliance with test parameters.

          - Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

          - Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.  Remove malfunctioning units, replace with new units, and retest.

          - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

        - Remove and replace malfunctioning units and retest as specified above.

      - CLEANING

        - Each pipe section shall be cleaned internally after preparation and before assembly by means of swabbing, using a suitable nonflammable cleaner. Pipe network shall be free of particulate matter and oil residue before installing nozzles or discharge devices.

      - SYSTEM FILLING

        - Preparation:

          - Verify that piping system installation is completed and cleaned.

          - Check for complete enclosure integrity.

          - Check operation of ventilation and exhaust systems.

        - Filling Procedures:

          - Fill extinguishing-agent containers with extinguishing agent and pressurize to indicated charging pressure.

          - Install filled extinguishing-agent containers.

          - Energize circuits.

          - Adjust operating controls.

      - DEMONSTRATION

        - Train Owner's maintenance personnel to adjust, operate, and maintain clean-agent and automatic fire suppression systems.

END OF SECTION