SECTION 23 0553

IDENTIFICATION FOR HVAC PIPING AND EQUIPMENT

PART 1 GENERAL

- SECTION INCLUDES

- RELATED REQUIREMENTS

- Section 09 9123 - Interior Painting: Identification painting.

- Section 22 0553 Mechanical Identification

- REFERENCE STANDARDS

- ASME A13.1 - Scheme for the Identification of Piping Systems; The American Society of Mechanical Engineers; 2007 (ANSI/ASME A13.1).

- BS 381C - Specification for colours for identification, coding and special purposes

- BS 1710 Identification of pipelines and services

- BS 5378 Part 1, Safety Signs and Colours - Specification for Colour

- Design HVCA DW 144 Specification for sheet metal ductwork

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements for submittal procedures.

- List: Submit list of wording, symbols, letter size, and color coding for mechanical identification.

- Product Data: Provide manufacturers catalog literature for each product required.

- Manufacturer's Installation Instructions: Indicate special procedures, and installation.

- Project Record Documents: Record actual locations of tagged valves.

PART 2 PRODUCTS

- REFER TO SECTION 22 0553 MECHANICALIDENTIFICATION

- IDENTIFICATION APPLICATIONS

Air Handling Units:  Nameplates.

Air Terminal Units:  Tags.

Automatic Controls:  Tags. Key to control schematic.

Control Panels:  Nameplates.

Dampers:  Ceiling tacks, where located above lay-in ceiling.

Ductwork:  Nameplates.

Heat Transfer Equipment:  Nameplates.

Instrumentation:  Tags.

Major Control Components:  Nameplates.

Piping:  Pipe markers.

Pumps:  Nameplates.

Relays:  Tags.

Small-sized Equipment:  Nameplates.

Tanks:  Nameplates.

Thermostats:  Nameplates.

Valves:  Tags and ceiling tacks where located above lay-in ceiling.

Water Treatment Devices:  Nameplates.

DUCTWORK IDENTIFICATION

Ductwork shall be colour coded in accordance with HVAC Specification DW142 to the colours indicated in Table 2.  For conditioned air, identification shall comprise either of two symbols (one red, one blue) or a single symbol coloured, part red, part blue.

TABLE 2

DUCT IDENTIFICATION COLOURS

| Type | Colour | BS 4800 |
| --- | --- | --- |
| Conditioned Air Fresh Air Exhaust / extract re-circulated air | Red and Blue Green Grey | 04353 / 18E53 14E53 AA009 |

According to BS 4800:

Direction of flow shall be by PVC self-adhesive equilateral triangles with one apex pointing in the direction of flow.  The minimum length of side of the triangle shall be 150mm.

PART 3 EXECUTION

- REFER TO SECTION 22 0553 MECHANICAL IDENTIFICATION

END OF SECTION