SECTION 23 0548

VIBRATION AND SEISMIC CONTROLS FOR HVAC PIPING AND EQUIPMENT PART 1 GENERAL

- SECTION INCLUDES

- Equipment support bases.

- Vibration isolators.

- Roof curbs.

- Requirements for sound and noise control shall as per ASHRAE standards

- Any conflict between ASHRAE standards and below sections, the higher specifications shall followed.

- Any additional verifications sound and noise improvement based on final site majors shall be taken into consideration as part of contractor scope of work

- RELATED REQUIREMENTS

- Section 01 4533 - Code-Required Special Inspections.

- Section 03 3000 - Cast-in-Place Concrete.

- REFERENCE STANDARDS

- ASCE 7 - Minimum Design Loads for Buildings and Other Structures; 2010, with 2013 Supplements and Errata.

- ASHRAE (HVACA) - ASHRAE Handbook - HVAC Applications; American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc.; 2011.

- IAS AC172 - Accreditation Criteria for Fabricator Inspection Programs for Structural Steel; International Accreditation Service, Inc.; 2011.

- SMACNA (SRM) - Seismic Duct Restraint Manual Guidelines for Mechanical Systems; Sheet Metal and Air Conditioning Contractors' National Association; 2008.

- ASHRAE Practical Guide to Seismic Restraint

- Uniform Building Code Seismic Zone 2B

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements, for submittal procedures.

- Product Data:

- Provide manufacturer's product literature documenting compliance with PART 2 PRODUCTS.

- Shop Drawings and Calculations:

- Provide schedule of vibration isolator type with location and load on each.

- Fully dimensioned fabrication drawings and installation details for vibration isolation bases, member sizes, attachments to isolators, and supported equipment.

- Include auxiliary motor slide bases and rails, base weights, inertia bases, concrete weights, equipment static loads, support points, vibration isolators, and detailed layout of isolator location and orientation with static and dynamic load on each isolator.

- Include selections from prescriptive design tables that indicate compliance with the applicable building code and the vibration isolator manufacturer's requirements.

- Clearly indicate the load and capacity assumptions selected. Include copies of any calculations.

- Include the calculations that indicate compliance with the applicable building code UBC Zone 2B the vibration isolator manufacturer's requirements.

- Manufacturer's Instructions: Indicate installation instructions with special procedures and setting dimensions.

- QUALITY ASSURANCE

- Perform design and installation in accordance with applicable codes.

- Designer Qualifications: Perform design under direct supervision of a Professional Engineer experienced in design of this type of work and registered and licensed in the State in which the Project is located.

- Manufacturer Qualifications: Company specializing in manufacturing products specified in this section, with not less than ten years of documented experience.

- Installer Qualifications: Company specializing in performing the work of this section with minimum five years of experience.

- Testing Agency Qualifications: Independent firm specializing in performing testing and inspections of the type specified in this section.

- See Section 01 4533 for additional requirements.

PART 2 PRODUCTS

- PERFORMANCE REQUIREMENTS

- General:

- All vibration isolators, base frames and inertia bases to conform to all uniform deflection and stability requirements under all operating loads.

- Steel springs to function without undue stress or overloading.

- Steel springs to operate in the linear portion of the load versus deflection curve over deflection range of not less than 50 percent above specified deflection.

- Lateral to vertical stiffness ratio to not exceed 0.08 with spring deflection at minimum 75 percent of specified deflection.

- All equipment mounted on vibration isolated bases to have minimum operating clearance of 50 mm (2 inches) between the base and floor or support beneath unless noted otherwise.

- 6. All restraining devices shall be tested and certified rating from OSHPD. Devices should have a preapproval number from OSHPD. Calculations to support seismic

restraint designs must be stamped by a registered professional engineer with at least 10 years of seismic design experience and licensed.

- 7. Seismic specialist shall provide professional indemnity insurance to cover design

and calculations.

- EQUIPMENT SUPPORT BASES

A. Structural Bases:

- Construction: Engineered, structural steel frames with welded brackets for side mounting of the isolators.

- Frames: Square, rectangular or T-shaped.

- Design: Sufficiently rigid to prevent misalignment or undue stress on machine, and to transmit design loads to isolators and snubbers.

- Applications: Adjustable motor slide rails for centrifugal fans.

- Concrete Inertia Bases:

- Construction: Engineered, steel forms, with integrated isolator brackets and anchor bolts, welded or tied reinforcing bars running both ways in a single layer.

- Size: 152 mm (6 inches) minimum depth and sized to accommodate elbow supports.

- Mass: Minimum of 1.5 times weight of isolated equipment.

- Connecting Point: Reinforced to connect isolators and snubbers to base including template and fastening devices for equipment.

- Concrete: Filled on site with minimum 20 mPa (3000 psi) concrete. See Section 03 3000 for additional requirements.

- Applications: Adjustable motor slide rails for centrifugal fans.

- VIBRATION ISOLATORS

A. Non-Seismic Type:

- All Elastomeric-Fiber Glass Pads:

- Configuration: Flat or molded.

- Thickness: 6 mm (0.25 inch) minimum.

- Assembly: Single or multiple layers using bonded, galvanized sheet metal separation plate between each layer with load plate providing evenly distributed load over pad surface.

- Elastomeric Mounts:

- Material: Oil, ozone, and oxidant resistant compounds.

- Assembly: Encapsulated load transfer plate bolted to equipment and base plate with anchor hole bolted to supporting structure.

- Steel Springs:

- Assembly: Freestanding, laterally stable without housing.

- Leveling Device: Rigidly connected to equipment or frame.

- Restrained Steel Springs:

- Housing: Rigid blocking during rigging prevents equipment installed and operating height from changing during temporary weight reduction.

- Equipment Wind Loading: Adequate means for fastening isolator top to equipment and isolator base plate to supporting structure.

- Elastomeric Hangers:

- Housing: Steel construction containing elastomeric isolation element to prevent rod contact with housing and short-circuiting of isolating function.

- Incorporate steel load distribution plate sandwiching elastomeric element to housing.

- Spring Hanger:

- Housing: Steel construction containing stable steel spring and integral elastomeric element preventing metal to metal contact.

- Bottom Opening: Sized to allow plus/minus 15 degrees rod misalignment.

- Combination Elastomeric-Spring Hanger:

- Housing: Steel construction containing stable steel spring with elastomeric element in series isolating upper connection of hanger box to building structure.

- Bottom Opening: Sized to allow plus/minus 15 degrees rod misalignment.

- Thrust Restraints:

- Housing: Steel construction containing stable steel spring and integral elastomeric element installed in pairs to resist air pressure thrusts.

- Bottom Openings: Sized to allow plus/minus 15 degrees rod misalignment.

23 0548 - 5

- ROOF CURBS

A. Vibration Isolation Curbs:

- Non-Seismic Curb Rail:

- Location: Between existing roof curb and rooftop equipment.

- Construction: Aluminum.

- Integral vibration isolation to conform to requirements of this section.

- Weather exposed components consist of corrosion resistant materials.

- Non-Seismic Curb:

- Location: Between structure and rooftop equipment.

- Construction: Aluminum.

- Integral vibration isolation to conform to requirements of this section.

- Weather exposed components consist of corrosion resistant materials.

- PIPE RISERS

- PIPE ANCHORS

1. All-directional acoustical pipe anchor, consisting of two sizes of steel tubing separated by a minimum 1/2" (12mm) thick 60 durometer neoprene. Vertical restraint shall be provided by similar material arranged to prevent vertical travel in either direction. Allowable loads on the isolation material should not exceed 500 psi (.35 kg/mm2) and the design shall be balanced for equal resistance in any direction.

- PIPE GUIDES

1. Pipe guides shall consist of a telescopic arrangement of two sizes of steel tubing

separated by a minimum 1/2" (12mm) thickness of 60 durometer neoprene. The height of the guides shall be preset with a shear pin to allow vertical motion due to pipe expansion or contraction. Shear pin shall be removable and reinsertable to allow for selection of pipe movement. Guides shall be capable of "1 5/8" (41mm) motion, or to meet location requirements.

PART 3 EXECUTION

- INSTALLATION - GENERAL

- Install in accordance with manufacturer's instructions.

- Bases:

- Set steel bases for 25 mm (one inch) clearance between housekeeping pad and base.

- Set concrete inertia bases for 50 mm (2 inches) clearance between housekeeping pad and base.

- Adjust equipment level.

- On closed spring isolators, adjust so side stabilizers are clear under normal operating conditions.

- Prior to making piping connections to equipment with operating weights substantially different from installed weights, block up equipment with temporary shims to final height. When full load is applied, adjust isolators to load to allow shim removal.

- Provide pairs of horizontal limit springs on fans with more than 1.5 kPa (6.0 inches WC) static pressure, and on hanger supported, horizontally mounted axial fans.

- Support piping connections to equipment mounted on isolators using isolators or resilient hangers for scheduled distance.

- Up to 100 mm (4 Inches) Pipe Size: First three points of support.

- 125 to 200 mm (5 to 8 Inches) Pipe Size: First four points of support.

- 250 mm (10 inches) Pipe Size and Over: First six points of support.

- Select three hangers closest to vibration source for minimum 25 mm (1.0 inch) static deflection or static deflection of isolated equipment. Select remaining isolators for minimum 25 mm (1.0 inch) static deflection or 1/2 static deflection of isolated equipment.

- FIELD QUALITY CONTROL

- See Section 01 4000 - Quality Requirements, for additional requirements.

- Inspect isolated equipment after installation and submit report. Include static deflections.

- Perform testing and inspections of the installation in accordance with Section 01 4533.

END OF SECTION