- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section

      - SUMMARY

        - Section Includes

          - The Contractor shall provide an IP closed circuit television (IPCCTV) system and accessories, complete and operable, in accordance with the following specifications, drawings, BOQs and Contract Documents.

          - Electrical and mechanical systems including rough-in, pathways, conduit, boxes and backboards.

          - The Contractor shall supply, install and commission IP CCTV system as ONE package, having the following as a minimum:

          - Network Video Recorders

          - Digital (IP) color camera, fixed, dome type- indoor.

          - Digital (IP) color camera, fixed, outdoor with wall bracket/ pole.

          - LCD Displays

          - CCTV systems Consoles & Racks

          - All accessories & sundries

      - REFERENCES

        - IEC.

        - NEC 	National Electrical Code; Article 800 Communication Circuits.

        - BS.

        - Local Codes, Standards and Regulations

        - Requirements of Local Authorities Having Jurisdiction.

        - LEED requirements.

      - SYSTEM DESCRIPTION

        - Surveillance IPCCTV system is required to ensure effective surveillance of an area as well as create a tamperproof record for post event analysis. The System shall provide an online display of video images on LED monitors located at security room.

        - System should facilitate viewing of live and recorded images and controlling of all cameras by the authorized users present in the LAN.

        - System should provide inter-operability of hardware, OS, software, networking, printing, database connectivity, reporting, and communication protocols. System expansion should be possible through off-the-shelf available hardware.

        - Proposed IP CCTV system shall be an open standard based integrated system with IP network centric functional and management architecture aimed at providing high-speed manual/automatic operation for best performance.

        - System shall use video signals from various types of indoor/outdoor IP CCD color cameras installed at different locations, process them for viewing on workstations/monitors at Asset’s Security room.

        - Mouse-Keyboard shall be used for Pan, Tilt, Zoom, and other functions of desired cameras.

        - System shall have digital CCD Color Video Cameras with individual built-in IP address, Network Video recorders (NVR/CAMERA SERVER), Network attached storage (NAS)/ Raid backup device for recording, Application software, Color Video Monitors, workstation for System Administration/ Management/ Maintenance etc.

        - The recording resolution and frame rate for each camera shall be user programmable.

        - Surveillance IPCCTV System shall operate on 240 V, 50 Hz single -phase power supply.

        - All the control equipment’s e.g. servers, NVR/CAMERA SERVER, NAS/Raid backup device, etc. shall be provided in standard Racks.

        - Security Room will have workstation along with controllers for Camera operation. For monitoring purposes, Video monitors/ LCD monitors shall be setup with suitable mounting arrangements, as per user requirements. Facility for viewing and controlling all the cameras at various other locations, as required, shall be provided.

        - There shall be a Control System with Video Control Software to manage all the video surveillance devices.

        - At any stage of construction, the Engineer may ask the Contractor to provide more cameras at additional costs. The Contractor’s system shall be capable of reasonable expansion.

        - In certain areas of the building there should be both fixed and motorized cameras, the fixed cameras shall cover totally the required area, the motorized cameras will be used in emergency case and focusing.

        - NVR at shall have enough HD capacity for recording of all cameras for minimum 31 days.

        - The system components shall be locked and shall be accessed only to authorized person.

        - CCTV camera external Power supply: External Power supply / Transformer within metal box are included in price of those cameras which need external power supply.

        - Observation Criteria

          - The selection of camera and lens for any location shall be based on certain observation criterion. The observation criterions are classified into four general categories which are based on the relative size of 1 6-meter-tall person appearing on a monitor screen:

            - Monitor & Control:  The relative size of the person as seen on the screen shall be minimum 5% of the screen height.

            - Detect:  The relative size of the person as seen on the screen shall be minimum 10% of the screen height.

            - Observe: The relative size of the person as seen on the screen shall be minimum between 25% and 30% of the screen height.

            - Recognize: The relative size of the person as seen on the screen shall be minimum 50% of the screen height.

            - Identify:  The relative size of the person as seen on the screen shall be minimum 100% of the screen height.

        - Live Viewing Requirement

          - All live viewing shall be real time and of high resolution. The resolution of the CCTV monitors used shall exceed the highest resolution camera used.

          - The number of monitors in the control room will depend on the number of cameras,

          - For IP CCTV systems all live viewing shall be minimum 4 CIF / 25 frames per second

      - SUBMITTALS

        - The Contractor shall submit the followings:

          - Company Profile.

          - Experience/ Commitments:

            - Similar work experience of installing IP CCTV systems: The bidder shall illustrate the references of IP CCTV systems projects to prove his capabilities and experiences in designing, supplying, installing, testing, commissioning, maintaining, and supporting the systems, and supporting the client in any requirements needed post-project handover. This should include case studies describing the following:

              - Case Study Reference Number.

              - Project Name.

              - Client Name.

              - Project Location.

              - Project Value.

              - Project Duration.

              - Scope of Work.

              - Customer Support.

              - Challenges & Lessons Learnt.

            - Minimum of one case study shall be presented for each of the below, following the above format:

              - Experience in similar development segment (i.e. Hotels, retail, mixed-use, residential, etc.).

              - Experience in Jordan

              - Experience in providing fully integrated solutions of IP CCTV systems.

              - Experience in enhancing IP CCTV systems.

            - Current commitments/ obligations: The bidder shall present all current commitments and obligations in the following format:

              - Project Name.

              - Client Name.

              - Project Location.

              - Project Duration and Target Start & End Dates.

              - Scope of Work.

            - Confirmation to having fully equipped & staffed local administration office & Engineering service center.

            - Confirmation to having local service center.

            - Other supporting information that adds value to the proposal.

          - Strategy for QA/QC:

            - QA/QC approach/procedure documents: The bidder shall provide a detailed description of QA/QC policies, method statements, procedures, people, resources, and forms used to manage IP CCTV systems design &/or installation projects.

            - Testing procedures: The bidder shall provide a detailed description of testing policies, method statements, procedures, program, people, resources, forms and sub-contractors used to manage each of the following testing procedures.

              - Factory acceptance tests (FAT).

              - Pre-installation tests.

              - Site acceptance tests (SAT).

              - User tests and user-defined customization.

              - 3rd party tests to be provided by both the vendors, Contractor witnessed by the Engineer.

            - Commissioning of works: The bidder shall provide a detailed description of commissioning of works’ method statements, procedures, program, and forms.

            - Completion & acceptance certificate: The bidder shall provide the certificate forms that would be issued for completion of works and acceptance of works. The forms should include a list of statements to any additional matters and/or concerns that have been raised as part of the works.

            - Examples of installation & record drawings: The bidder shall provide an example of IP CCTV systems installation and record

            - Drawings generated for a similar project.

            - O&M Manuals: The bidder shall provide an example of O&M Manuals generated for a similar project.

            - Software used to define optimal position of IP CCTV systems components: The bidder shall provide a detailed description of the software used to define the optimal position of the IP CCTV systems components by analyzing aspects such as coverage areas, low vs. high density areas, etc....

            - QA-ISO 9001:2008 registration or equivalent.

            - Other supporting information that adds value to the proposal.

            - Site Survey

              - Site visit declaration.

          - Functional Analysis: The analysis should comply with all the requirements set in the Contract and with local authorities. Outcome of analysis should include:

            - Observation criteria and surveillance requirements of each CCTV camera.

            - Objective, functionality, and surveillance requirements of Security Management Application.

            - Objective and functionality of NVR.

            - Identify CCTV monitoring rooms and mission-critical (back-up) sites, objective, functionality, and surveillance requirements of each of these sites.

            - Other supporting information that adds value to the proposal.

          - System layouts and wiring drawings and diagrams including:

            - Layout drawings of entire system including containment layouts.

            - Sectional drawings of entire system.

            - Schematic diagram for entire system.

            - Layout drawing of the Secured Cabinet.

            - Power Distribution Drawing.

            - Layouts for IP CCTV systems control rooms and equipment rooms– distances from IP CCTV systems devices to and across these rooms.

            - Layout for power supply from main supply room and distribution boards across the IP CCTV systems components.

            - Functionalities and snapshots of IP CCTV systems Management software application.

            - Other supporting information that adds value to the proposal.

          - Technical Details.

            - Detailed description of proposed solution.

              - Type of CCTV system proposed; IP.

              - Non-Compatible Standard Encoding and Streaming.

              - Number and Locations of the cameras.

              - Types of cameras and specifications (resolution, format, fps, etc.).

              - Outdoor/Indoor requirements.

              - Space in server racks available in main security room.

              - Camera mounting type considering a decent aesthetic design suitable for the project.

              - Lens type.

              - Technical data sheets of all equipments, software and materials.

            - Detailed list of Equipment & Software

            - Detailed list of Materials

            - All civil, MEP and support works, including and not limited to:

              - Containment.

              - Cabling.

              - Scaffolding and access ladders.

              - Labor.

              - Power supply.

              - Other tools & services.

            - Unless advised otherwise, Contractor is self-supportive and should include for his offer his own materials, tool, services, office, and any requirement necessary to complete this project.

            - Provide samples of each of the system’s proposed devices; indoor/ outdoor/ fixed/ CCTV cameras, monitoring screens, camera mounting bracket, fittings, accessories, ..etc and as requested by the Engineer together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

            - Coordination with other parties.

              - Method statement for installation, testing, commissioning and operation of proposed system.

              - Scope of work matrix for all works listed in this Contract Deliverables Section.

              - Communication protocol.

            - Outline risk assessment for all major aspects of the works.

            - General method statement/risk assessment on approach to day to day responsibilities.

            - List of Spare parts to be provided for minimum 10 years.

            - Item by Item commentary on technical requirements.

            - The Contractor shall comply with all specifications described in the Technical Specification sections herein. System specifications proposed should reflect each of the system components in question, functionality desired by the system component and the how the component integrates with the centralized system. The Contractor shall add 3 columns beside each item to state the following:

              - First column is ‘Bidder’s Compliance’: Contractor shall specify here one of the below:

                - Y: proposal does comply with specification/requirement.

                - N: proposal does not comply with specification/requirement.

                - N/F: proposal does not fully comply with specification/requirement.

                - N/A: specification/requirement is not applicable to the project.

              - Second column is ‘Reference’:

                - Contractor shall refer each compliant item to the related section of proposal, such as IP CCTV systems.

                - Component data sheet or reflected electrical/ceiling/wall plans layout drawing.

              - Third column is ‘Bidder’s Comments’:

                - Contractor shall note down any further description, comment, feedback, concern, etc. on each item.

                - Contractor shall note down any further description, comment, feedback, concern, etc on each item.

            - Vendor certificates:

              - Company certification by vendor as authorized dealer.

              - Personnel certificate by vendor as factory-trained.

              - Product quality assurance certification by vendor.

            - Vendor list and selection criteria for all items, vendors should adhere to the following criteria:

              - Company established at least 10 years ago.

              - Have references of at least 20 projects globally of similar scope & complexity.

              - Based in Jordan since at least 5 years.

              - Have references of at least 5 projects in Jordan of similar scope & complexity.

              - Have a local support office.

              - Have a local warehouse for spare parts stocking.

            - Proposed subcontractors identified and scope of work for each.

            - Confirmation of guarantee periods for equipment and guarantee terms & conditions.

            - Confirmation of warranty periods for equipment and guarantee terms & conditions.

            - Maintenance & support offering – sufficient details.

            - Other supporting information that adds value to the proposal.

          - Bidder’s Compliance Letters.

            - Conformity of bid to requirements – sufficient technical details.

            - Conformity to agree on Confidentiality Agreement.

            - Letter of Bidder’s Compliance with All Specifications.

            - Conformity of responsibility to secure Compliance with related government/utility authority.

          - List of Proposed Personnel with CVs & Responsibility Matrix.

            - Relevant experience for key team members.

            - Other supporting information that adds value to the proposal.

          - Schedule of Works: Bidder shall compile a schedule of works and include a project milestone as per Master Schedule of Works provided. It is up to the bidder to create a schedule that best incorporates all works.

          - Handover & Close-Out Documentation.

            - As Built Drawings.

            - End User Manuals.

            - Maintenance Manual.

            - Operations Manual.

            - Plans as mentioned above.

            - S/W license, update and upgrade .procedures.

            - Other supporting information that adds value to the proposal.

          - Shop drawings and catalog data submittals shall be made in accordance with relevant sections. The Contractor shall submit sufficient information to indicate the scope and quality of the IP closed circuit television (CCTV) installation.

            - Block diagram showing system relationships of major components and quantities and interconnecting cable requirements.

            - Plans showing equipment locations, conduit, and conductor requirements.

            - Control console and panel arrangements, equipment outlet devices, and special mounting details.

            - Wiring diagrams showing terminal identification for field-installed wiring.

            - Catalog literature with camera and monitor specifications.

            - Spare parts list.

            - Method Statement for installation, connection, testing and commissioning the system.

            - The contractor shall submit layout plans showing coverage zone of each camera in the project. In-case of any place covered by more than one camera, overlapping shall be achieved between coverage zone of those cameras without having any blind area, this shall be clearly shown on the Contractor’s submitted drawings using color coding For the Engineer approval.

          - The Contractor shall furnish operating service manuals for the system.  The manuals shall be bound in flexible binders and all data contained therein shall be printed or typewritten. Each manual shall include all instruction necessary for proper operation and receiving of the system, and a complete block diagram of the system, a complete circuit diagnosis of the system, and a wiring designation schedule for the camera, as well as other major components, and a replacement parts list.

          - The Contractor shall submit 6 set of Operation & Maintenance manuals complete with preventive maintenance schedules, procedures and troubleshooting procedures.

          - The Contractor shall meet all project requirements, yet he is required to submit to the Engineer for his approval a proposal for an upto date technology system.

          - AS-BUILT DRAWINGS: Submit the number of sets of final as-built schematic drawings as indicated in the contract documents highlighting locations all components included in the system complete with labels.

      - CLOSEOUT SUBMITTALS

        - Comply with requirements of Division 01.

        - Project Record Documents: Record actual locations of cameras and routing of television cable.

        - Operation and Maintenance Data: Submit instructions for operating system and performing routine trouble shooting procedures.

      - MANUFACTURER & INSTALLER QUALIFICATIONS

        - IP CCTV system components shall be manufactured by firms that are regularly engaged in the production of IPCCTV camera, monitors, and auxiliary equipment similar to that required for this project and that have been satisfactory service for at least 10 years.

        - The firm installing the IPCCTV system shall have had a minimum of 5 years documented prior successful installation experience with IPCCTV systems similar in scope to the system of this project.

        - The system shall be engineered, configured, commissioned and serviced by manufacturer's certified systems integrator employing certified personnel for design and installation of the system. Materials and equipment shall be the catalogued products of manufacturers regularly engaged in production of access control equipment and the products proposed shall be the latest versions commercially available at the time of the bid.

        - The manufacturer shall be ISO-9002 and ISO 9001 certified for Quality Assurance in Production, Installation and Servicing.

        - The systems integrator shall be an authorized partner to the manufacturer and the partnership shall be at least two year old. The manufacturers - system integrator combination shall have implemented at least three projects of similar complexity in Jordan.

        - Contractor Qualification

        - Manufacturer Qualification

      - QUALITY ASSURANCE

        - The Contractor shall post a note, at the camera and monitor station, to indicate the name, address, and telephone number of the firm to call when service is necessary.  Note shall be mounted in a metal frame attached to the camera case.

        - Operation of the IPCCTV system shall be demonstrated to the Engineer to prove, under normal conditions, that coverage complies with this specification.

        - Reference Demonstration: System Integrators would be asked to demonstrate a working IP CCTV system as per the document specifications to prove their ability to comply with Project requirements. The  proof-of-concept  demonstration  of  the proposed IP CCTV system shall be as follows:

          - Location: IP CCTV system / command center reference site using a solution proposed by the System Integrator.

          - Configuration: The installed solution is expected to be exposed as much as possible for physical examination.

          - Real-Time Demonstration:

            - The integration of all components specified in this document should be demonstrated in real-time as a working system. More references could be used to demonstrate different components, depending on the projects’ scope.

            - Demonstration of events, alerts, reporting, scheduling of events, Management application and other possible functions of the IP CCTV system are required.

      - PRE-INSTALLATION MEETINGS

        - Convene minimum one week prior to commencing work of this section.

      - ENVIRONMENTAL REQUIREMENTS

        - Conform to manufacturer’s standard service conditions during and after installation of components.

      - FIELD MEASUREMENTS

        - Verify field measurements prior to fabrication.

      - SPARE PARTS

        - Supply as maintenance stock, consumable devices, components as recommended by Supplier, but shouldn’t be less than two units of each type/ rating of installed consumable material/ component/ device, incase less than three numbers of devices/ material are installed, minimum of one unit of each type/ size/ rating of each device/ material shall be provided as spare stock.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Three Engineers. Training shall be sufficient enough to enable the Engineers to carry out day-to-day operation, maintenance and software and hardware administration of the system without or with minimal assistance from the vendor’s technical staff.

        - Engage a factory-authorized service representative, whose credentials are approved by the Engineer, to explain programming and operation of systems and to train Employer's maintenance personnel on procedures and schedules for maintaining, programming, operating, adjusting, troubleshooting, and servicing system.

        - Training shall be carried out to an approved training manual Separate training shall be provided on the hardware and software. Each training shall have both class room session and hands on session. Contractor shall allow for 6 trainees each in both the trainings.

- PRODUCTS

      - INDOOR DOME/ BULLET  IP CAMERA (DAY/NIGHT )

- Minim requirement

          - Up to 5 megapixel (2592 × 1944) resolutions.

          - Standard video compression with high compression ratio.

          - Progressive scan CMOS, capture motion video without incised margin

          - Support dual stream, and the sub-stream for mobile surveillance

          - High-performance and long service life Infrared LED,

          - Approx. 10 to 30 meters IR range

          - Two-way audio(-S)

          - POE (Power over Ethernet)

          - Built-in Micro SD/SDHC/SDXC card slot, up to 64 GB

          - FPS: up to 25-30

      - HIGH DEFINITION OUTDOOR FIXED IP CAMERA

        - General

          - The outdoor camera dome system shall provide a 100Base-TX network interface for live streaming to a standard Web browser.

          - The outdoor camera fixed system shall be a discreet camera dome system consisting of a dome drive with a variable speed/high speed pan/tilt drive unit with continuous 360 rotation; 1/3”, 1/2” high resolution color, CMOS camera; motorized zoom lens with optical and digital zoom; auto focus; and an enclosure consisting of a back box, lower dome, and a quick-install mounting.

          - Note: ¼” is unacceptable as image quality deteriorates substantially with a smaller chip.

          - The outdoor network positioning camera shall support standard IT protocols.

          - The outdoor network positioning camera shall feature open architecture connectivity for third-party software recording solutions allowing integration into virtually any IP-based system.

          - The cameras should exceed 75% integration with a minimum of 15 VMS platforms.

          - The cameras should be SMPTE (Society of Motion Picture and Television Engineers) Compliant. SMPTE compliant cameras offer full frame rate at HD resolution (720/1080p), good color fidelity, and wide screen (16:9) format.

          - The outdoor fixed dome system shall meet or exceed the following design and performance specifications:

        - Electrical Specifications

          - Ports: RJ-45 for 100Base-TX Auto negotiate/Manual setting	Auto MDI/MDI-X

          - Cabling: Cat6A cable or better for 100Base-TX

          - Input Voltage:18 to 32 VAC; 24 VAC nominal 22 to 27 VDC; 24 VDC nominal

          - Input Power

          - 73 VA nominal (with heater)

          - 3 A nominal (with heater)

          - Alarm Outputs for 35X SE: 7No.

          - Auxiliary Outputs for 35X SE:2Nos.

        - Video Specifications

          - Video Encoding: H.264 base profile, MPEG-4, MJPEG

          - Video Streams 3, simultaneous, to comply with backup regulations.

          - Frame Rate shall be not less than 30.  Frame Camera shall have the feature to adjust its Frame Rate to  25, 24, 15, 12.5, 12, 10, 8, 7.5, 6, 5, 4,3, 2, 1 (dependent upon coding, resolution, and stream configuration)

          - Supported Protocols	TCP/IP, UDP/IP (Unicast, Multicast IGMP), UPnP, DNS, DHCP, RTP, RTSP, NTP, IPv4, SNMP, QoS, HTTP, HTTPS, LDAP (client), SSH, SSL, SMTP, FTP, mDNS (Bonjour®)

          - Users 20 simultaneous using unicast; unlimited using multicast H.264 or MPEG-4 802.1x (EAP)

          - Software Interface Web browser view and setup, up to 16 cameras

          - Open IP Integration.

          - The cameras should exceed 75% integration with a minimum of 15 VMS platforms.

          - Resolution: High Definition, not less than 8 Miga pixels.

        - Dome Drive: The variable speed/high speed pan/tilt dome drive unit shall meet or exceed the following design and performance specifications:

          - Pan Speed Variable between 400 per second continuous pan to 0.1° per second

          - Vertical Tilt Unobstructed tilt of +2 to –92

          - Manual Control Speed Pan Speed of 0.1 to 80 per second, and pan at 150 per second in turbo mode. Tilt operation shall range from 0.1 to 40 per second

          - Automatic Preset Speed Pan speed of 400 and a tilt speed of 200 per second

          - Presets:

          - 35X SE 256 positions with a 20-character label available for each position; configurable camera settings, including selectable auto focus modes, iris level, LowLight™ limit, and backlight compensation for each preset; command to copy camera settings from one preset to another; and preset configuration through control keyboard or through dome system on-screen menu

          - Preset Accuracy	± 0.1

          - Proportional Pan/Tilt Speed ,Speed decreases in proportion to the increasing depth of zoom

          - Automatic Power Up.  35 SE, User-selectable to the mode of operation; the dome will resume when power is cycled, including an automatic return to position or function before power outage

          - Zones 8 zones with up to 20-character labeling for each, with the ability to blank the video in the zone

          - Motor Drive Cogged belt with 0.9° stepper motor

          - Motor Operating Mode Microstep to 0.015° steps

          - Motor Continuous duty and variable speed, operating at 18 to 32 VAC, 24 VAC nominal

          - Limit Stops: 35X SE, Configurable for manual panning, auto/random scanning, and frame scanning

          - Inner Liner Rotating black ABS liner inside a sealed lower dome

          - Patterns. 35X SE -8 user-defined configurable patterns including pan/tilt/zoom and preset functions, and pattern configuration through control keyboard or through dome system on-screen men

          - Pattern Length User-defined length based on dome memory

          - Internal Clock Internal system clock, user configurable for 12- or 24-hour day format and mm/dd/yy or dd/mm/yy calendar format

          - Scheduler Internal scheduling system for configuration presets, patterns, window blanks, alarms, and auxiliary functions based on internal clock settings

          - Autosensing	Automatically sense and respond to protocol utilized for controlling the unit

          - Menu System Built-in setup of configurable functions and multiple languages including English and Arabic

          - Auto Flip Rotates dome 180° at bottom of tilt travel

          - Password Protection Configurable settings with optional password protection

          - Clear individual, grouped, or all configured settings

          - Freeze Frame Freeze current scene of video during preset movement

          - Display Setup User-definable locations of all labels and displays and user-selectable time duration of each display

          - Azimuth/Elevation/Zoom On-screen display of pan/tilt locations and zoom ratio

          - Compass Display On-screen display of compass heading and user-definable compass setup

          - Camera Title Overlay 20 user-definable characters on the screen camera title display

          - Video Output Level User-selectable for normal or high output levels to compensate for long video wire runs

          - Dome Drive Compatibility All dome drives are compatible with all back box configurations

          - RJ-45 Jack Contains a plug-in jack on the dome drive for control and setup of the unit, the uploading of new operating code and language file updates, and is compatible with personal computers

          - Remote Data Port  Compatibility Ability to set up and control unit, and upload new operating code and language file updates through the easily accessible optional remote data port; remote data port is also compatible with personal computers

          - Power Consumption Maximum 70 VA

          - The high definition CMOS camera shall meet or exceed the following design and performance specifications:

        - Color Optic System (35x)

          - Image Sensor minimum 1/2’’- 1/3” CMOS sensor.

          - Scanning System Interlace/Progressive selectable

          - Effective Pixels	: 2592 (H) x 1944 (V) or 5Mega pixels.

          - Resolution Scaling: Down to 352 x 240

          - Lens f/1.4 (focal length, 2.8~12 mm; 35X optical zoom, 15X digital zoom)

          - Configurable Zoom Speeds 3.2, 4.6, or 6.6 seconds

        - Back Box And Lower Dome

          - The back box and lower dome shall meet or exceed the following design and performance specifications:

          - Connection to Dome Drive Quick, positive mechanical and electrical disconnect without the use of any tools

          - Trap Door Easy access trap door that allows complete access to the installation wiring, providing complete separation of the wiring from the dome drive mechanics when closed

          - Terminal Strips Removable terminal strips with screw-type terminals for use with 22-14 gauge wire

          - Auxiliary Connections 1 Form-C relay output up to 40 VAC or 40 VDC at 2 A maximum 1 open-collector output up to 32 VDC at 150 mA maximum

          - Alarm Inputs

            - 35X SE, 27X SE (Models) 7 alarm inputs

            - 23X SL (Model)	1 alarm input

          - Installation Quick-mount wall, corner, pole, parapet, or ceiling adapter

          - Cable Entry Through a 1.5-inch NPT fitting

          - Environmental Features Factory-installed heaters, blowers, and sun shroud

          - Operating Temperatures Maximum temperature range of –60 to 140F   (–51° to 60°C) for two hours and a continuous operating range of –50° to 122F (–45° to 50°C)

          - Memory Built-in memory storage of camera and location-specific dome settings such as presets and patterns; if new dome drive is installed in back box, all settings will automatically download into new dome drive

          - Color Neutral, baked-on enamel powder coat

          - Construction Aluminum

          - Lower Dome Material Acrylic, optically clear, with no distortion in any portion of the dome up to +2 above the horizon

          - Dome Color Clear and smoked versions

          - Trim Ring Connection 2 screws

          - Safety Cable Plastic tether

        - Certifications And Ratings

          - CE, Class B, FCC, Class B, UL/cUL Listed,C-Tick

          - 2.NEMA Type 4X, IP66

      - NETWORK  VIDEO RECORDER NVR SERVER  (WITH MANAGEMENT SOFTAWRE)

        - The NVR shall be available as a rack mountable standalone device with onboard hard disk recording and incorporate the following features:

          - Recording capacity of the NVR system shall be 31 days on D1 4CIF resolution.

          - D1 resolution may be H.264 or MPEG4 format.

          - System supplier shall determine hard disk capacity of NVR according to above conditions.

          - Operating system of the NVR may be Linux or windows based system.

        - Administration will be performed through a web page and support the configuration of following parameters:

          - Name and Location.

          - Maximum recording chunk file size

          - Maximum recording chunk age

          - Minimum free disk space (typically 5% of total disk space).

          - IP Address configuration.

          - Ethernet Interface speed.

          - Time configuration by Real Time Clock configuration or Network Time Protocol (NTP).

          - NTP Server configuration

          - Disk Status including disk temperature monitoring

          - Administration is also possible using the Console serial port.

        - The NVR must support system logging to a remote IP address, console port or the unit itself.

        - The NVR must provide dedicated web pages for diagnostic output including:

          - Current Media Connections (by IP address)

          - Local System Log

          - Registry Information

          - Boot Log

          - System Processes

          - Device Information

          - Interrupt Information

          - Network Statistics

          - Serial Port Statistics

        - The NVR must provide an RS232 console port for debug output and serial configuration.

        - The NVR must provide Telnet access for further diagnostics. This is permitted only to administrators with the administrator password with an IP address specified on the Firewall.

        - Standalone Enterprise NVR;

        - 32ch-POE- 1080P HD IPC input & recording,

        - 8ch 1080P playback, 512Mbps output bandwidth, mpeg-4 compression.                                                                Forward, reverse (speed 32 x) - step by step and different speed play.

        - RJ45 Ethernet, RS485, HDMI, VGA and USB (can display different)

        - Include H.D Minimum 4T.B

      - CENTRAL MANAGEMENT SOFTWARE

        - General

          - The Central Management Software shall provide the ability to simultaneously connect to not less than ten, sixteen-channel Digital Video Recorders. Each camera shall have the ability to be individually programmed to display in live or playback mode. This feature allows the user to view live video and search multiple sites up to Forty-eight Cameras at the same time. Other features shall include event logging, The security video system shall be an IP network-based, fully distributed digital video system. The security video system will utilize local area networks (LAN) as a transmission medium for video, configuration, as well as storage of all data. The security video system shall provide full video control at the building, with additional full selection capability at any point within the network from a workstation or a video console display. The security video system shall provide unlimited expansion capability for the addition or modification of video inputs. The VMS system shall not be license based and shall not have any cost for upgrade of software or firmware.  The system shall be expandable to unlimited video inputs   The VMS and the cameras should preferably come from the same manufacturer to make sure there is no mix-match solution or non-compatibility or performance sacrifice.

          - The Contractor shall furnish and install all security video cameras, cameras, mounts, housings, power supply systems, coaxial cable, network cables, connectors, equipment racks, monitors and consoles, computer controlled network switchers, work stations, network video recorders, encoders, decoders, video console displays, and all other hardware and software to provide a fully operational system The security video system shall permit normal and event monitoring of all secured areas on DVI or LED monitors as required or shown in the specifications and drawings  Video monitoring consoles shall be installed at the main control room and as shown on the drawings and described in these specifications   In all cases, the equipment shall be state of the art, standardized commercial off-the-shelf, and modular  In all cases, the method of communication from remote locations within the network to the central components shall be transparent to the user  Equipment shall be selected and installed so repairs may be accomplished on site by module replacement, utilizing spare components whenever possible.

          - The intent of this specification is to provide the Engineer with a distributed networked digital security system Supplied by the Contractor, the security video system shall be complete and operational per the performance requirements and objectives of these specifications. The Contractor shall be responsible for the coordination of related work with other trades affecting his/her work or the work of others.

        - Codes And Standards

          - Work shall be performed in accordance with the applicable national and local codes or standards current at the commencement of installation. The following list summarizes the applicable codes and standards:

            - National Electrical Safety Code, current edition

            - National Fire Protection Association National Fire Codes, current edition

            - EIA/TIA–568 Commercial Building Telecommunications Wiring Standard

            - EIA/TIA–569 Commercial Building Standard for Telecommunications Pathways and Spaces

            - EIA/TIA–606 Administrative Standards for the Telecommunications Infrastructure of Commercial Buildings

            - IEEE, RS 170 variable standard

            - NTSC/PAL

            - IEEE, 802 3 digital data network standard

            - EIT/TIA–568A premises cabling standard

            - Member, Universal Serial Bus (USP) Implementers Forum

            - Compliant with ISO/IEC 14496 standard (also known as MPEG-4) Compliant with International Telecommunication Union (ITU) Recommendation G 711, “Pulse Code Modulation (PCM) of Voice Frequencies”

          - When more than one code or regulation is applicable, the more stringent regulation shall apply

        - Video Security System Capabilities

          - The IP video security system network shall be arranged so each area will operate independently and shall communicate to the system manager through no less than a 1000BaseT Gigabit Network.   The IP video security system shall utilize virtual matrix switcher capabilities through the use of a system manager.  The system manager shall provide a user interface and database management of the IP video security system.  System manager software shall allow for the restriction of users to logical configurable groups of cameras, monitors and system operations.

          - The system manager shall be capable of performing as a NTP Server for the entire system.  The IP video security system shall be synchronized to an NTP server so that all system components function on the same time clock basis.  The NTP server shall reside within the system, and it shall be capable of being driven by external time sources if needed.  All time-zone corrections shall automatically be provided in the system.

          - The system manager shall be capable of performing as a DHCP and UPnP server for the entire system and components. The system manager shall provide all connection and management communications between system devices.

          - The system manager shall be capable of incorporating RSA 256 bit public/private key authentication in addition to custom bit public/private keys The IP video security system shall be capable of authenticating any video produced by the encoder that was originally produced by the stream, NVR recording the stream, or operator who exported the stream; all shall include time/date stamped video

          - The system manager shall manage rights and permissions for all devices, persons, and any system video or other data. The IP video security system’s digital recording and monitoring system shall incorporate a fault tolerant architecture and shall include redundancy in critical areas of concern Encoder power supplies and NVR/storage box power supplies shall be capable of redundancy.   As a standard, all NVRs and storage boxes shall provide RAID 5/6 redundancy in the event of any system failure RAID 6 should be used for installations with more than 100 cameras.

          - The IP video security system shall provide an API/SDK that is capable of being used at a level consistent with a full-featured gateway.

          - The IP video security system shall provide multilevel diagnostics of each component in all critical areas.  These diagnostics shall be reported to a diagnostic console for processing. The diagnostic data shall be capable of being scripted into actionable events within the system. The diagnostics shall be capable of being mined by network diagnostic systems such as Open View, Tivoli, and others.

          - The IP video security system shall be able to handle future expansion of an unlimited total capacity from what is shown in the drawings, including but not limited to cameras, monitors, alarm circuits, and relay closures.

        - Basic System Capabilities

          - The following capabilities are considered essential for the IP video security system described in this specification.

          - The IP-based video security system software shall provide a built-in digital video virtual matrix switcher.  The IP video security system shall support the ability to switch any camera in the system to any monitor in the system, through either a PC keyboard/mouse or a joystick controller to either an analog or HDMI Monitor.

          - The IP video security system shall be an integrated hardware and software platform.  It shall provide distributed administration of multiple devices and administer rights and privileges for all attached devices.

          - The system manager shall manage system security, functioning as a key manager for user and device authentication.  It shall also route communication between all devices on large, sub-netted security networks. The system manager shall store and administer secure keys and shall have multilevel and user permission management.

          - The system manager shall function as the default system time network video recorder, using the industry standard NTP protocol to ensure integrated devices are synchronized. The system manager shall support UPnP architecture and shall provide DHCP services, supporting the dynamic addition of network devices.

          - The system manager shall store a database of device errors, alarms, and other system events.

          - The comprehensive database shall be accessed and searched through the system log window. The system manager shall allow for connection to an intelligent uninterruptible power supply (UPS), and it shall allow for a message to be sent to the UPS in the case of a power failure. The system manager also supports data replication; a duplicate set of critical system data can be stored on a second system manager, enabling quick and easy transition to IP video security equipment.

          - The IP video security system encoders, workstations, cameras, monitors, alarms, relays, etc., shall be configurable.

          - The system manager shall provide for an unlimited number of system operators with personal identification numbers (PINs) that define priority levels, operator facilities, system roles, and camera and monitor groupings.

          - The IP video security system shall have the capability of the following functionalities:

            - The system shall be fully distributed in nature so that each system device can remain operational in a majority of modes without dependence on other devices.

            - Multiple users shall be able to simultaneously view the same camera view or sequence. The system shall utilize multicast streaming video to allow multiple users to view the same video stream, though not necessarily synchronized with each other, without affecting the bandwidth of the network Video titling shall provide for a 100-character camera site description (on/off), display time/date (on/off), set the display color (black-white), display a site message (on/off), and define the screen block position for the title.

          - The IP video security system shall be able to capability to create and execute a system script used to control any system function, and it may be combined into any order. The configuration of such scripts shall be easy to use and follow the rules of drag and drop configuration.  The IP video security system shall be capable of the following actions (minimal requirements):

            - Display video from any camera to a specific monitor or screen division, including changing screen division views.

            - Reset any monitor to its original screen division and image

            - Start/stop recording an event from any indicated video source

            - Utilize script nesting, a means of running another script within any given script

            - Activate system relays and send e-mail notification to any recipient through pop3

            - Add wait times to any script command.

          - The scripting language shall utilize a system function upload and will modify or send out a global command to all components in the system.

          - Operator control of a camera or selection of monitors shall override the   sequence control of camera or monitor; sequence control of cameras or selection of monitors shall not override operator control of camera of selection of monitors.

          - The IP video security system shall allow for programming of alarms and associated incoming alarms with related parts of the system.

          - Individual, group, or all alarms shall be disabled by special sequences, which can be initiated by the operator or automatically by time/day/date.

          - The IP video security system shall log all alarms and events in the system manager database.

          - The IP video security system shall provide real time system status on the operator graphical user interface (GUI)  All alarms, current monitor activity,.

          - The IP video security system shall be capable of the following languages: English, Arabic, French, Spanish, German, Portuguese, Italian, Russian, and Chinese (simple). The system also shall be capable of accepting new language packages from one central point. The system shall allow for user profiles, by language, to be loaded into any operational location including workstations and virtual matrix controllers.

        - Network Storage Manager

          - In large and multi-building developments, a Network Storage Manager (NSM) is required.  The NSM either replaces or integrates with NVRs/DVRs to centrally manage the entire development

          - The network storage manager shall record video and audio streams from IP cameras and video encoders on the network.

          - The network storage manager shall incorporate the server functions and storage elements into a purpose-built chassis.

          - The network storage manager shall use RAID 6 parity across the storage drives to protect recorded data against a hard disk drive failure

          - The network storage manager shall only use enterprise-level hard disk drives specifically rated for operation in RAID systems.

          - The network storage manager chassis shall be designed for video surveillance recording applications and encompass redundancy at all vital points:

            - Hot swappable hard drives

            - Redundant, hot swappable power supply modules

            - Redundant, hot swappable system fans

            - Hot swappable O/S drive

            - Hot swappable CPU fans

          - The network storage manager chassis shall be designed for online service and maintenance and cannot be removed from the rack when hard disk drives, fans, power supplies, or operating system drives must be replaced.

          - The network storage manager shall be built upon a reliable and robust Linux® operating system

          - The network storage manager shall support a guaranteed recording throughput of 250 Mbps per storage device with a minimum of 64 Mbps of read throughput. This throughput shall be guaranteed under normal and error (RAID rebuild) conditions.

          - The network storage manager shall support any number of cameras so long as the maximum throughput required is less than 250 Mbps.

          - The network storage manager shall support the recording of MPEG-4 and H 264 baseline, and high profile streams from standard resolution and megapixel cameras.

          - The network storage manager shall support continuous, scheduled, alarm/event (including analytics alarms), motion, and manual recording.

          - Pre- and post-alarm periods shall be configurable up to the total capacity of the system

          - The network storage manager shall support bookmarking and locking/unlocking of video content on the drives.

          - The network storage manager shall support privacy tools that allow administrators to establish maximum retention times for normal, alarm, and locked video.

          - The network storage manager shall support an intelligent video grooming protocol that can reduce the frame rate of recorded video as the video ages.  Administrators shall have the flexibility to determine whether to groom alarm video or leave it at its real-time level.

          - The network storage manager shall have the ability to report all diagnostic events, including software status diagnostics to a centralized user interface.  In addition, Simple Network Management Protocol (SNMP) traps shall be available for monitoring through a third-party SNMP management console.

          - The network storage manager shall be fully managed from a remote workstation, including the ability to configure settings and update firmware and software.

          - The network storage manager shall be capable of interfacing with any smart UPS using a USB connector.  The network video recorder shall receive status and control signals from the uninterruptible power supply (UPS) when it is in backup mode. This function shall inform the operator about the amount of charge remaining and trigger a controlled shutdown when the charge becomes zero.

          - The network storage manager shall meet or exceed the following design and performance specifications:

          - It would be possible to configure the Network storage manager with active-active failover, hot-stand-by failover or on-demand failover, redundant or mirrored .It should be capable of using Multi-cast streams from the camera for recording  This would save a lot of bandwidth on bandwidth-critical installations.

          - Multiple NSM’s or video servers shall feature clustering and provide distributed storage architecture featuring active-active failover and load balancing.  Distributed storage servers shall act as one large virtual storage pool, able to be accessed with one virtual IP address.  This shall make sure that in a large environment where the camera quantity is huge, failure of one or two NSM’s or video servers shall automatically load balance and re-distribute the cameras between the available NSM’s or video servers.  This shall happen automatically without operator intervention. When failover happens or NSM’s fail, live view of cameras shall never stop on monitors.

            - POWER SPECIFICATIONS

              - Power Input: 100 to 240 VAC, 50/60 Hz, auto-ranging

              - Power Supply: Internal, dual-redundant, hot-swappable

              - prongs, molded connector

            - ENVIRONMENTAL SPECIFICATIONS

              - Operating Temperature: 50° to 95°F (10° to 35°C) at unit air intake

              - Operating Humidity: 20% to 80%, non-condensing

              - Maximum Humidity Gradient : 10% per hour

              - Operating Altitude: –50 to 10,000 ft (–16 to 3,048 m)

              - Operating Vibration: 0 25 G at 3 to 200 Hz at a sweep rate of 0 5 octave/minute

            - SYSTEM SPECIFICATIONS

              - System

                - System Drive: Linux Compact Flash system drive

                - RAID Level: RAID 6 for storage drives

                - Effective Capacity: Up to 18 4 TB

                - Drive Interface: SATA/SATA II

              - Network

                - Interface 2, 1 Gigabit Ethernet RJ-45 ports (1000Base-T)

                - Security 2 modes: secure mode (device authentication) and unsecured mode

                - Auxiliary Interfaces

                - x2 USB 2.0 Ports on rear panel

                - x1 USB 2.0 port on front panel

            - CERTIFICATIONS  1 CE, Class A

              - FCC, Class A

              - UL/cUL Listed

              - C-Tick

              - S Mark for Argentina

              - CCC/CQC

            - WARRANTY: Minimum 3 years, parts and labor

        - Video Management Software

          - Shall be an open platform IP based security management software which supports IP cameras from different manufacturers

          - Shall not be client-server based so that failure of one component or critical component does not halt the entire system for instance, failure of one Network Storage Manager or System Manager shall not stop other storage managers from recording or stop streams of live videos onto the monitors It should be possible to start or stop any device without affecting the performance of the other components

          - Multiple video servers/storage managers shall act as one large virtual server  Such a feature shall eliminate the risk of one or number of  servers failing together at the same time  Multiple servers shall operate in a large virtual pool or cluster   This large virtual pool/cluster should be accessible with one virtual IP address  It should feature active-active failover and load balancing as standard   Failure of one or two members of the pool/cluster shall, automatically load balance and redistribute the cameras between the available servers  Once a failover happens, there shall be a buffer storage for a minimum of 1 day to make sure that old data does not start to over write immediately

          - Shall be able to display 16 IP cameras simultaneously for live viewing and playback

          - Shall be centrally managed, fully scalable and secure There shall be any limit on number of cameras or clients that can be connected to the system

          - Shall provide a built-in command script editor that allows customized command script to be written to control virtually all the system functions

          - Shall have the ability to automatically assign IP addresses to IP cameras, NVRs etc

          - Shall display video analytics from IP cameras

          - Shall display analytic alarms from cameras that have on-board analytics

          - Shall support displaying video analytic alarms on the proper site maps

          - Shall support digital zoom on live & recorded videos

          - Shall support dual monitors for displaying the maps and cameras

          - Shall scan the complete network for IP cameras, NVRs, workstations etc and setup system tree indicating all detected items

          - Shall have GUI to allow live and archived images from multiple remote systems to be viewed on the client workstation.  The operator shall monitor and supervise various locations simultaneously with complete flexibility in selecting and viewing live and recorded images

          - The GUI shall display systems floor plan selection & navigate among different maps and site plans

          - The Contractor shall customize the navigation and layouts as requested by the user

          - The navigation tools shall support one or two step selection from site map to floor plan

          - Linking of maps of maps to track people shall be supported

          - Shall support drag & drop of cameras from the system tree & maps

          - GUI shall support minimum of 10 maps.

          - hall support simultaneous viewing of recorded video from multiple client workstations without affecting the ongoing recording

          - Shall support backup on DVD-WR and through the USB 2 0 ports

          - The DVD backup shall be viewable on standard windows media player / real player for non-encrypted use.  For encrypted use it will be acceptable to have it played on special software loaded on the same DVD with the required video clip

          - Shall have auto system recovery after power failure; auto re-booting, auto scan & recover of data

          - Shall have auto configuration wizard for cameras, user profiles etc

          - Shall support video loss alarm.

          - Management & configuration tools shall be included to configure & manage IP cameras, NVRs, workstations which are connected to the system

          - Shall support displaying single, quad, nine, twelve or sixteen images of cameras, each at 25 fps @ VGA, 4CIF   It should also decode high definition and full-high-definition streams

          - Shall support viewing multiplexed images of IP cameras with the capability of selecting individual camera.

          - Site Map with IP camera location, for easy camera selection & selective viewing of either live or playback or recorded cameras shall be supported

          - User selectable display pattern of single, quad or multiple IP camera format to simultaneously display live or playback of archived video at the NVR or local video storage on the IP camera shall be possible

          - Setup and termination of connections between IP camera, NVRs, workstations via drag and drop from either a system tree or site map, to display live and/or playback video on a single multi window patterns screen, selective viewing and control of single cameras shall be supported either by clicking on the camera icon on the site map or on the system tree

          - Shall have playback controls; such as play, pause, forward, backup etc

          - Shall support archived video retrieving search by IP number, time, date, selected object, intelligent motion detection etc

          - Shall support still image export to JPEG and BMP format with date & time stamp

          - Shall support local & remote alarm notification by email, SMS, for alarms, minor & major faults

          - Shall support saving logs of all users & system activities and interactions

          - Shall show the bandwidth consumption for single & multiple IP cameras

          - Shall support text insertion for any desired video clip for easy retrieval

          - Shall support general & customized reports generation

          - Shall support graphical map creation & editing, importing of customized maps, attaching IP camera icons etc

          - Shall have SDK / API for integration of 3rd Party equipment

          - Shall support adding users, assigning passwords & access rights to various client applications

          - User selectable image capture rates either on an all-input basis or input by input basis. The capture ate feature may be programmed to automatically adjust the capture rate on the occurrence of an external alarm or an internal event

          - Selectable image resolution either on an all-input basis or input by input basis. The image resolution feature may be programmed to automatically adjust the image resolution on the occurrence of an external alarm or an internal event

          - Compression methods determine quality of playback H 264 hardware compression offers fast transfer rates over the internet with high quality video

          - Motion detection or any analytics shall be done at the camera to avoid any additional load on the servers

          - Routing of input video to video monitors based on user inputs or automatically on alarms or events

          - Input, time and date stamping   51  Alarm and event logging on appropriate video inputs

          - Alarm and event search

          - One or more sound recording channels.

          - Archival

          - Selecting a fixed camera.

          - User log on/off.

          - Making shift log Bidder’s Comments.

          - Image management (send image to spot monitor, send image to monitor wall)

          - Monitor wall image management (setting default images)

          - Spot monitor image management (setting default images, setting quad images)

          - Adjusting recording settings (frame rates, storage durations)

          - Set view parameters (contrast, brightness, color etc)

          - Guide tours management (adding, deleting and modifying)

          - View recordings (select, start, stop, forward, rewind, pause etc)

          - Set time and date   66  Set camera reference   67  Set image title   68  Images file management (deleting files, re-naming files, copying files)

          - System configuration (adding and deleting cameras)

          - Operator profiles (accessing date/time/duration of use, adding and deleting users)

          - Access to engineering settings.

          - Commonality of design between different monitored areas within the same development

          - It should be possible to stitch different cameras on the export player so that it is easy for gathering evidence and perform playback on all cameras simultaneously

          - It should be possible to support ASCII interface as well as interface using external I/O ports

          - ASCII interface provides greater flexibility to integrated with fire alarm panels, BMS etc

          - The ability to software select on an IP Megapixel camera between its maximum resolution and the various resolutions below it (i e 4CIF, 2CIF, CIF, D1, etc )

          - Software features should include but not necessarily limited to the above

      - HIGH RESOLUTION COLOR MONITOR

        - The LED color monitors shall provide a high resolution picture; high quality; 100% steel housing; front panel controls; built-in speaker; connections for video and audio input/output, including separate Y-C connectors for S-VHS input.

        - The color monitor shall meet or exceed the following specifications:

          - Diagonal Picture: As per BOQ inches

          - Standards: NTSC/PAL

          - TV Lines of Resolution	Minimum of 700 horizontal TV lines

          - Input Power Range : 90-260 VAC, 50/60 Hz

          - Speaker	: 1.0 W (-3 dBV), built-in

          - Comb Filter	: Digital

          - Color Switching: Automatic between NTSC/PAL formats

          - Composite Video Voltage:  1.0 Vp-p

          - Synchronization: Internally derived

          - Front Panel Controls: Tint, color, brightness, contrast, volume, and power on/off

          - Connector Inputs: 2 BNC inputs, 2 looping outputs, 1 DIN S-VHS

          - Audio Inputs: 2 RCA inputs

          - Output Connectors: 1 looping output

          - Operating Temp. Range:  0° to 41°C

          - Operating Humidity Range:  0% to 90% relative, non-condensing.

          - Certifications: CE, Class B; UL; cUL; FCC, Class B

      - SOFTWARE PROTOCOL AND LICENSES

        - Software shall be provided to operate the cameras from the CCTV control rooms. The software may be proprietary but it shall have an open protocol and it shall meet all the operational requirements. The license shall permit the client in the future to employ competent persons to modify the software without having to obtain the approval of the program authors Sufficient software licenses shall be provided for the client to operate the CCTV system.

        - The Contractor shall provide a detailed summary of the facilities that the proposed software offers identifying the operating system, typical screen displays, typical control functions, typical data input facilities and typical output reports.

      - NETWORK SWITCH

        - Network Switches will have ports per number of digital feeds, will support 100 Mbps/1Gbps communication and are required to support 802.1x standards.

      - FIREWALLS

        - The firewall shall have the capacity to support layer 3-4 secure rule base enforcement; it also shall support IPS (intrusion prevention) abilities and gateway level anti vandal abilities, and with a support of state full inspection features.

        - The installed firewall will act as the system encryption termination point since it shall support AES-256 IPSEC encryption.

        - The Firewall installed in the system cabinet will be connected to the public network, using a separate special 1Gbps communication line (throughout SFP fiber port).

      - VIDEO ENCRYPTION

        - It is required that all video streams transported on the Wide Area Network (WAN) will be 256 AES Encrypted.

- EXECUTION

      - GENERAL

        - All materials and equipment shall be installed in accordance with the manufacturers printed recommendations and the requirements of the Contract Documents. Equipment shall be installed, adequately ventilated, and securely anchored.

        - If the raceway indicated does not conform to the requirements of the IPCCTV system, provided, it is the Contractor’s responsibility to modify the raceway system as acceptable to the Engineer.

      - WORKMANSHIP

        - Conductor terminations at screw terminals shall be accomplished with hooked, spade lugs. Shielding shall be continuous & shall be grounded at the monitor which shall be frame grounded. Wiring shall be cabled within enclosures and banded neatly to terminals.

      - INSTALLATION

        - Units shall be mounted to maximize coverage of the main entrance area. Wiring throughout the system shall be identified in accordance with approved shop drawings; identification shall be applied at all terminations and access fittings. Connections to monitor shall be waterproof and flexible and shall be accomplished with cable connectors.

      - EXECUTION OF TEST PROCEDURES

        - The Contractor shall operate all equipment, in the presence of the Engineer. Operation shall demonstrate the IPCCTV system performance is satisfactory for lighting conditions encountered during normal plant operation. At completion of test all adjustments shall be locked or sealed.

- END OF SECTION