- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - REQUIREMENTS

        - All general provisions contained herein or within any other section of the Specifications shall be fully applicable to each and every other section.

        - Works on all the Installation shall be carried out in a neat, efficient and workmanlike manner, assuring satisfactory/ proper operation, maintenance and repair. The work shall be in accordance with the requirements of these Specifications, and shall fulfill their true intent and meaning. No deviations from these Specifications and Drawings shall be made without written approval of the Engineer.

        - These Specifications and associated drawings form a composite set of documents, intended for the selection and installation of equipment having the general and specific characteristics as detailed.

        - Unless otherwise specifically stated, the installation shall be left complete, tested and ready for operation in all respects and fully integrated and coordinated with all other construction.

        - The Contractor is responsible for getting Local Utilities/ Service Providers and the Engineer on any system prior to system material ordering/ manufacturing or installing, approvals shall be in the format of acceptance letters, signed shop drawings to be submitted to the Engineer. In-case any electrical system after being ordered/ manufactured or installed, be rejected/ not accepted by the Local Utility/ service provider/  by the related service provider/ Authorities or the Engineer , the Contractor shall dismantle the system, replace with new approved one at his own cost without any compensations from the Engineer. The Contractor will also be responsible for all time delay resulted from this.

        - The Comply with regulations and requirements.

        - The Contractor shall obtain relevant Ministry approvals on drawings and materials, and inspection by the authorities, in scheduled sequence to obtain connection of services to the building in accordance with the approved construction schedule. If required

        - The electrical systems/ device/ component is inclusive of all material, accessories, supports, fixings, suspensions, metal stands/ platforms, concrete foundations, ..etc needed for the proper installation and operation of the system even if not shown on the drawings or mentioned in the bill of quantities, whether the system is numerated or in lump sum.

        - The Contractor shall submit proof, that the materials, appliances, equipment or devices that he furnishes and installs under this contract, meet the requirements of Local Authority, BS and NFPA as regards to fire and casualty hazards.

        - The electrical system is inclusive of all parts, devices, software, programming, licensing, calibration, adjustment, setting, necessary for the best functional operation of that system, whether mentioned in the drawings, specifications, BOQ or not .

        - Details, elevations and sections of electrical substation, generators’ rooms, electrical/ IT rooms / Risers shown on the electrical drawings are for guidance only, yet the contractor shall provide detailed dimensional layouts, sections, elevations work shop drawings for each of these rooms/ risers.

        - Cable trays/ cable Ladders and manhole shown on the drawings are indicative, the contractor shall provide all needed cable trays/ cable ladder / manholes / UPVC duct for cables wiring, whether shown/ mentioned or not in the drawings/ bills of quantities, the cable trays/ ladders / manholes / UPVC duct shall be of enough size to install all cables on maintaining clear distance between any two cables installed on equals twice of the largest cable’s diameter. Wherever additional lengths/ sizes needed cable trays/ ladders are not shown on the drawings or not covered in the bill of quantities or due to rerouting of any cables they (the cable trays/ Ladders/ UPVC duct/ manholes ) shall be considered to form part of the contract.

      - SCOPE OF WORK

        - The work under this division of the Specifications shall include furnishing all labour, materials, equipment and services to install the complete electrical system, putting into operation, tested and commissioned as shown on the Drawings and specified herein. The work includes, but is not limited to, the following principal systems and equipment:

          - Co-ordination of incoming utilities (electricity and telephone supplies).

          - Low Voltage Power Distribution System including LV distribution boards, LV cables, panel boards, cables containment etc.

          - Emergency Power Generation and Distribution System including standby generator, Automatic Transfer Switch (ATS) panel

          - Un-interruptible Power Supply System.

          - Electrical Installations serving all mechanical plants (HVAC & Plumbing) including all LV cabling, trays, disconnect switches and connections to equipment. Electrical Installations serving all special systems and equipment provided under other divisions of the specifications such as elevators, and other electric-operated equipment.

          - All kinds of electrical raceways, boxes, manholes,  UPVC duct , and fittings.

          - All kinds of wiring devices, dimmers, disconnect switches, starters, electric meters, etc.

          - Interior, exterior, emergency, exit, street, flood, façade and other special lighting.

          - Earthing/ Grounding and Bonding systems.

          - All low current / Extra Low Voltage and security systems, fire alarm system, as detailed in the Contract documents.

          - Any other works mentioned elsewhere in the project electrical specification sections.

      - ELECTRICAL SUPPLY

        - The Low Voltage Electrical Power Supply shall be 3 phase, 4 wire, 50 Hertz earthed neutral system.  The voltage rating shall be 400/230 Volts, 50 Hertz. Power distribution system shall be 3 phase, 5 wire, 50 Hertz system

      - STANDARDS

        - The complete Electrical services shall be designed and installation in accordance with good practice, and following standards:

          - British Standards BS.

          - The International Electro Technical Commission (IEC).

          - NFPA (for fire and Life safety systems).

          - Any requirements stated within the Specifications.

          - The IEE Wiring Regulations, 17th Edition with all current additions and amendments.

          - Local Electrical/ Telecom utilities/ service providers\ Municipality requirements.

          - ANSI/ASHRAE/IESNA STANDARD 90.1-2010

          - Local standards

          - Any special requirements of separate earthing for low current systems as per project specifications, drawings, relevant standards and manufacturer’s recommendations.

      - EARTHING REQUIREMENTS

        - The earthing system shall in all respects comply with the following:

        - The earthing system shall take the form of (TT) system for the electrical installations of the project. The Contractor must ensure that the installation of earthing system complies with the requirements as laid down in section – “Earthing System” contained elsewhere in the Specifications.

        - The earthing conductor (the final conductor by which the connection to the selected means of earthing is made) shall be of copper construction and comply with the requirements of relevant standards.

        - All extraneous conductive parts of any equipment or building shall be protected by equipotential bonding in accordance with relevant standards.

      - LOW CURRENT & SPECIAL SYSTEMS REQUIREMENTS

        - Assign a specialist supplier/designer for all low current and special systems.

        - Specialist suppliers shall verify the design and submit shop drawings and materials based on the requirements of the construction documents and related international standards.

        - The shop drawings and as-built drawings shall be stamped by the suppliers.

        - The suppliers shall support their submittals with catalogues and satisfactory calculations.

        - Bear the cost of any extra item found necessary to have a properly functional system.

      - CO-ORDINATION

        - The contractor shall be solely responsible for the proper co-ordination of all phases of the Work and timely delivery to the site of all equipment and materials for proper execution of the Work.

        - Co-ordinate the Work with all or any other disciplines to ensure proper phasing and continuity of the Works. If it becomes necessary to remake any part of these Works or that of any other discipline or trade as a result of poor or badly timed co-ordination, then all costs associated with remaking those Works will be borne by the Contractor.

        - Co-ordinate with all supply undertakings and Authorities and shall include for attendance along with all costs involved in re-directing existing services.

        - Take into consideration all statutory and local requirements issued by the Electricity Supply Authority, Local Authority, Central Government, Broadcasting Authority, Telephone and Telecommunications Authorities along with any other requirements to be considered for the correct and legal operation of the Electrical and Telecommunication Installation or equipment connected to the Installation as part of this Contract. Pay all costs due to the requirements of any authority except for connection fees.

        - The Contractor shall be responsible for the co-ordination with all Electrical and Mechanical Systems’ Suppliers and shall include in his cost all the electrical requirements (even if they were not mentioned in the BOQ or drawings) to have a fully functional system as specified and as recommended by the Manufacturer or the codes. This is also applicable to all ancillary systems & equipment such as: Elevators, Kitchen Equipment, Audio-Visual, Low Current Systems and Security Systems.

      - CLIMATE CONDITIONS

        - External to the building and in non-air conditioned spaces, all apparatus shall be rated for an ambient temperature maximum of 40 oC, minimum of 1 oC,. In air conditioned buildings, all apparatus shall be rated for ambient temperature of 23 oC, maximum.

        - Altitude is around 700 m ASL.

        - When equipment is installed in direct sunlight, it shall either be shielded from direct radiation or suitably rated for additional solar gains. Cables shall always be shielded from direct sunlight.

        - All apparatus (except the generators) shall be rated for continuous service twenty-four hours a day, seven days a week throughout its normal rated life, except for necessary routine maintenance.

      - ACCESSIBILITY

        - All works within the project and particularly above suspended ceilings or inside vertical shafts shall be so installed as to be accessible for operation, maintenance and repair. Deviations from the drawings may be made to accomplish this, but no change shall be made without written approval from the Engineer. Locations of access doors and panels shall be approved by the Engineer before installation work is commenced.

      - STORAGE OF MATERIALS AND EQUIPMENT

        - All material and equipment, fixed or unfixed, shall be protected against corrosion, deterioration and ingress of foreign matter and moisture.

        - All material and equipment shall be kept clear of the floor or ground by means of wooden bearers and shall be protected against the weather with durable waterproof wrapping and other appropriate means.

        - The Contractor shall be liable for any loss due to delivery, storage or site security problems.

      - PREVENTION OF NOISE AND VIBRATION

        - Provision shall be made to minimize noise and vibration. However, different manufacturer's equipment will have varying sound and vibration characteristics. The contractor shall be responsible for ensuring that equipment installed does not transmit unnecessary noise or vibration.

        - All equipment installed in plant rooms and outside areas shall not be audible in the occupied areas.

        - Any vibration isolators, isolating bases, flexible connections, silencers, other acoustic treatment or anti-vibration precautions necessary shall be included in the rates for the equipment.

        - In individual cases, the suspension shall ensure that the natural frequency of the vibratory system in the vertical direction is not more than 1/3 of the exciter frequency and never exceeds 25 Hz.

        - Submit proof of the selected noise proofing measures to the Engineer before commencement of work.

        - Submit to the Engineer for information the noise level generation by the plant selected so that structural soundproofing measures can be evaluated. This means either data on the acoustic capacity level in relation to frequency, or the sound pressure level measured at 1 meter from the plant at octave median frequencies from 63 Hz to 4000 Hz. Details of the spatial and operational conditions shall also be given.

        - All costs of noise sound level measurements and any repeat measurements, necessary if acoustic requirements are not met, shall be allowed for by the Contractor.

        - Coordinate and comply with the requirements of noise control as applicable and as given in Section 23 05 48 – Vibration and Seismic Controls for HVAC Piping and Equipment.

      - GUARDS

        - All moving parts of machinery shall be protected by strong guards to adequately protect all personnel working on or in the vicinity of equipment. The guards shall be constructed in such a manner that the movement of drive belts and rotation of shafts may be readily observed without removal of the guard.

        - All 'live' parts of electrical equipment shall be protected in such a way to adequately protect all personnel working on or in the vicinity of equipment from injury.

        - Wherever possible, all protective guards shall be supplied by the Equipment Manufacturer. All guards shall be strongly attached to equipment and shall be designed to be easily removed for access, servicing, adjustment and maintenance.

      - SIGNS AND NOTICES

        - All signs and notices shall be in Arabic and English with the Arabic version being above or to the right of the English version.

        - A schedule of all signs and notices with proposed Arabic and English translations shall be approved by the Engineer prior to manufacture.

      - GOVERNING CONDITIONS

        - The entire Electrical Installation shall in all respects comply with the requirements of the latest editions of the following Standards, regulations and requirements with any current additions and amendments:

          - Local Standards.

          - Local Electrical Power Utility.

          - Local Telephone Service Provider.

          - International Electro-technical Commission.

          - IEE Wiring Regulations, 17th edition with all current additions and amendments.

          - British Standards (BS).

          - International Organization of Standardization (ISO).

          - National Fire Protection Association (NFPA).

          - Requirements or Standards stated elsewhere within this Specification.

          - Drawings and general provisions of the Contract, including General and Supplementary Conditions .

      - LABEL AND IDENTIFICATION

        - Each item of the Electrical Installation including electrical switchgear, control gear, equipment, devices, etc. shall be fitted with a non-corrodible label clearly indicating its function giving at least the following information:

          - Manufacturer’s name.

          - Country of origin.

          - Type / model number or code.

          - Rated voltage, current and frequency (as applicable).

          - Short circuit breaking capacity with time.

          - Compliance mark of the international standard(s).

        - Prior to final testing, confirm that all labeling is intact over the whole site and that all cables have been fitted with circuit markers. The 11,000 volts cables shall be clearly labeled "DANGER HIGH VOLTAGE" every two meters of their exposed length.

        - All conductors shall have their outer covering colored to suit the phase to which they are connected.

        - An instruction notice giving details of first aid treatment for electric shock shall be positioned in an approved position in each switch room. Manufacturer's or Contractor's names or trademarks shall not be exhibited anywhere through the installation without the prior approval and permission of the Engineer with exception that the Contractor's name and address may be fixed in an approved position on the main incoming switchgear.

        - All labels shall be in English and Arabic.

      - VERMIN PROOFING

        - All items of electrical equipment shall be adequately vermin proofed.

        - Where cables enter or leave the bottoms of switchboards, or pass through pipe ducts, they shall be sealed by the use of hard wood plugs treated with vermin repellent and surrounded by mastic sealant.

        - All spare pipe ducts shall be similarly sealed by the use of solid hard wood plugs.

        - Alternative methods of vermin sealing will be accepted, but the written comments of the Engineer must be obtained prior to installation.

      - FIRE AND SAFETY PRECAUTIONS

        - The whole of the works shall be carried out with care and so arranged as to minimize the risk of fire and the extent of damage resulting from any outbreak of fire.

      - PENALTY FOR DAMAGE TO EXISTING UTILITIES

        - Study the location of all the existing utilities and any other facilities, and perform the Work so as not to damage them.  In the event that any of such facilities are damaged by the Contractor, the same shall be immediately repaired by the Contractor at his cost and responsibility.

        - In the event that the Contractor damages the existing utilities or facilities listed below, the Contractor shall pay to the Client, in addition to the repair costs, an amount specified below:

          - Power Cable, Control Cable: An amount equal to one hundred percent and Instrument Cable (100%) of the actual repair costs.

          - Telephone Cable: An amount equal to one hundred percent (100%) of the actual repair costs.

          - Fresh Water Line: An amount equal to one hundred percent (100%) of the actual repair costs.

          - Sewer Line	:  An amount equal to one hundred percent (100%) of the actual repair costs.

      - SPARES AND CONSUMABLES

        - Unless otherwise mentioned elsewhere in electrical systems’ specifications, provide an unpriced list of spares and consumables to manufacturer’s recommendation for 2 years’ operation for every item of plant and system.

      - ELECTROMAGNETIC COMPATIBILITY

        - All equipment and systems installed under this Contract shall meet following specifications on electromagnetic compatibility:

          - Interference immunity according to BS EN 61000: Part 6-3.

          - Emitted interference according to BS EN 61000: Part 6-2.

        - The Contractor shall submit EMC Manufacturer assessment/ certificate for each and all electrical systems as a proof of their compliance with related international standards and regulations.

      - WARRANTY

        - Unless mentioned elsewhere under system’s related specifications, the Contractor shall warrant each system with all its components against manufacturing and workmanship defects for a period of One year (five years for lifts) from the date of practical completion certificate.

      - MAINTENANCE SERVICE

        - Service and maintain the installations as specified in Division 1 and detailed in these specifications.

        - Include periodic maintenance of systems as recommended by the manufacturer or supplier.

        - Inspect systems for proper operation and safety once every two months or
lesser period if recommended by manufacturer.

        - Provide on-call maintenance service for rectification of faults observed in the systems with response time not more than 24 hours for non-critical faults and 6 hours for faults affecting the continued use or safety of the building.

      - SUBMITTALS

        - In general the contractor shall as a minimum submit for each electrical system the followings in addition to all submittals requested elsewhere under electrical systems specification sections:

          - Company Profile.

          - Experience/ Commitments:

            - Similar work experience of installing each electrical system, The Contractor shall illustrate the references of electrical systems projects to prove his capabilities and experiences in designing, supplying, installing, testing, commissioning, maintaining, and supporting the systems, and supporting the client in any requirements needed post-project handover. This should include case studies describing the following:

              - Case Study Reference Number.

              - Project Name.

              - Client Name.

              - Project Location.

              - Project Value.

              - Project Duration.

              - Scope of Work.

              - Customer Support.

              - Challenges & Lessons Learnt.

            - Minimum of one case study shall be presented for each of the below, following the above format:

              - Experience in similar development segment.

              - Experience in Jordan.

              - Experience in providing fully integrated solutions of the systems.

              - Experience in enhancing the systems.

          - Current commitments/ obligations, The Contractor shall present all current commitments and obligations in the following format:

            - Project Name.

            - Client Name.

            - Project Location.

            - Project Duration and Target Start & End Dates.

            - Scope of Work.

          - Confirmation to having fully equipped & staffed local administration office & Engineering service center.

          - Confirmation to having local service center.

          - Other supporting information that adds value to the proposal.

        - Strategy for QA/QC:

          - QA/QC approach/procedure documents, The Contractor shall provide a detailed  description  of  QA/QC  policies,  method statements, procedures,  people, resources, and forms used to manage electrical system design &/or installation projects.

          - Testing procedures, The Contractor shall provide a detailed description of testing policies, method statements, procedures, program, people, resources, forms and sub-contractors used to manage each of the following testing procedures.

            - Factory acceptance tests (FAT).

            - Pre-installation tests.

            - Site acceptance tests (SAT).

            - User tests and user-defined customization.

          - Commissioning of works: The Contractor shall provide a detailed description of commissioning of works’ method statements, procedures, program, and forms.

          - Completion & acceptance certificate: The Contractor shall provide the certificate forms that would be issued for completion of works and acceptance of works. The forms should include a list of statements to any additional matters and/or concerns that have been raised as part of the works.

          - Examples of installation & record drawings: The Contractor shall provide an example of electrical system/s installation and record

          - Drawings generated for a similar project.

          - O&M Manuals: The Contractor shall provide an example of O&M Manuals generated for a similar project.

          - Software used to define optimal systems components sizes/ ratings/ positions.

          - QA-ISO 9001:2008 registration or equivalent.

          - Other supporting information that adds value to the proposal.

        - Site Survey

          - Site visit declaration.

        - Functional Analysis

          - The analysis should comply with all the requirements set in the Contract and with local authorities.

        - System layouts and wiring drawings and diagrams including:

          - Layout drawings of entire system including containment layouts.

          - Sectional drawings of entire system.

          - Schematic diagram for entire system.

          - Detailed wiring diagrams for all systems’ components.

          - Power Distribution Drawing.

          - Layouts for systems control rooms and equipment rooms– distances from system’s devices to and across these rooms.

          - Layout for power supply from main supply room and distribution boards across system’s components.

          - Functionalities and snapshots of system’s Management software application.

          - Other supporting information that adds value to the proposal.

        - Technical Details.

          - Detailed description of proposed solution.

            - Type of system proposed.

            - Non-Compatible Standard Encoding and Streaming.

            - Number and Locations of system’s components.

            - Types of system’s components and specifications.

            - Outdoor/Indoor requirements.

            - Spatial requirements for system’s components.

            - Mounting type/ height/ requirement considering a decent aesthetic design suitable for the project.

            - Technical data sheets of all equipments, software and materials.

        - Detailed list of Materials

          - All civil, MEP and support works, including and not limited to:

            - Containment.

            - Cabling.

            - Scaffolding and access ladders.

            - Labor.

            - Power supply.

            - Other tools & services.

          - Unless advised otherwise, contractor is self-supportive and should include for his offer his own materials, tool, services, office, and any requirement necessary to complete this project.

          - List of samples to be provided.

          - Coordination with other parties.

            - Method statement.

            - Scope of work matrix for all works listed in this Contract Deliverables Section.

            - Communication protocol.

          - Outline risk assessment for all major aspects of the works.

          - General method statement/risk assessment on approach to day to day responsibilities.

          - List of Spare parts to be provided for minimum 2 years (unless mentioned elsewhere under related system detailed specification section).

          - Item by Item commentary on technical requirements.

          - The Contractor shall comply with all specifications described in the Technical Specification sections herein. System specifications proposed should reflect each of the system components in question, functionality desired by the system component and the how the component integrates with the centralized system. The Contractor shall add 3 columns beside each item to state the following:

            - First column is ‘Contractor’s Compliance’:

              - Contractor shall specify here one of the below:

                - Y: proposal does comply with specification/requirement.

                - N: proposal does not comply with specification/requirement.

                - N/F: proposal does not fully comply with specification/requirement.

                - N/A: specification/requirement is not applicable to the project.

            - Second column is ‘Reference’:

              - Contractor shall refer each compliant item to the related section of proposal.

              - Component data sheet or reflected electrical/ceiling/wall plans layout drawing.

            - Third column is ‘Contractor’s Comments’:

              - Contractor shall note down any further description, comment, feedback, concern, etc. on each item.

          - Contractor shall note down any further description, comment, feedback, concern, etc on each item.

            - Vendor certificates.

              - Company certification by vendor as authorized dealer.

              - Personnel certificate by vendor as factory-trained.

              - Product quality assurance certification by vendor.

          - Vendor list and selection criteria for all items, vendors should adhere to the following criteria (unless mentioned elsewhere under system’s related detailed specification section):

            - Company established at least 10 years ago.

            - Have references of at least 20 projects globally of similar scope & complexity.

            - Based in Jordan since at least 5 years.

            - Have references of at least 5 projects in Jordan of similar scope & complexity.

            - Have a local support office.

            - Have a local warehouse for spare parts stocking.

          - Proposed subcontractors identified and scope of work for each.

          - Confirmation of guarantee periods for equipment and guarantee terms & conditions.

          - Confirmation of warranty periods for equipment and guarantee terms & conditions.

          - Maintenance & support offering – sufficient details.

          - Other supporting information that adds value to the .proposal.

        - List of Proposed Personnel with CVs & Responsibility Matrix.

          - Relevant experience for key team members.

          - Other supporting information that adds value to the proposal.

        - Full detailed calculations (using software) for systems’ components sizing, such as voltage drop calculations, power supplies ratings, amplifiers ratings, short circuit calculations at medium voltage and low voltage installations (at each equipment connected to the power network), protective devices/ breakers discrimination settings, protective devices/ breakers cascading calculations, closed loop impedance, protective relays calibration and settings for the substations, load summing, lighting levels in all spaces for selected light fitting types, ..etc, and any other calculations requested by the engineer related to any electrical systems used in this project.

        - Schedule of Works:

        - Contractor shall compile a schedule of works and include a project milestone as per Master Schedule of Works provided. It is up to the Contractor to create a schedule that best incorporates all works.

        - Shop drawings and catalog data submittals shall be made in accordance with relevant sections. The Contractor shall submit sufficient information to indicate the scope and quality of the proposed system installation.

          - Block diagram showing system relationships of major components and quantities and interconnecting cable requirements.

          - Plans showing equipment locations, conduit, and conductor requirements.

          - Control console and panel arrangements, equipment outlet devices, and special mounting details.

          - Wiring diagrams showing terminal identification for field-installed wiring.

          - Catalog literature with camera and monitor specifications.

          - Spare parts list.

          - Method Statement.

        - Handover & Close-Out Documentation.

          - As Built Drawings.

          - End User Manuals.

          - Maintenance Manual.

          - Operations Manual.

          - Plans as mentioned above.

          - S/W license, update and upgrade .procedures.

          - Other supporting information that adds value to the proposal.

        - The Contractor shall furnish operating service manuals for the system.  The manuals shall be bound in flexible binders and all data contained therein shall be printed or typewritten. Each manual shall include all instruction necessary for proper operation and receiving of the system, and a complete block diagram of the system, a complete circuit diagnosis of the system, and a wiring designation schedule for all systems’ components, and a replacement parts list.

        - The Contractor shall submit 6 set of Operation & Maintenance manuals complete with preventive maintenance schedules, procedures and troubleshooting procedures.

        - The Contractor shall meet all project requirements, yet he is required to submit to the Engineer for his approval a proposal for an up to date technology system.

        - As-Built Drawings

          - Submit the number of sets of final fully detailed dimensional as-built drawings and schematic diagrams highlighting locations, sizes and connections of all components included in the system complete with labels.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations/ installation heights of system components, pull boxes, and routing of its wiring.

        - Operation and Maintenance Data: Submit instructions for operating system and performing routine trouble shooting procedures.

      - MANUFACTURER & INSTALLER QUALIFICATIONS

        - Unless otherwise mentioned elsewhere under electrical systems related detailed specification the following shall be applied:

          - System’s components shall be manufactured by firms that are regularly engaged in the production of the proposed electrical system, and its auxiliary equipment similar to that required for this project and that have been satisfactory service for at least 10 years.

          - The firm installing the proposed electrical system shall have had a minimum of 5 years documented prior successful installation experience with systems similar in scope to the system of this project.

          - The system shall be engineered, configured, commissioned and serviced by manufacturer's certified systems integrator employing certified personnel for design and installation of the system. Materials and equipment shall be the catalogued products of manufacturers regularly engaged in production of system’s equipment and the products proposed shall be the latest versions commercially available at the time of the bid.

          - The Manufacturer shall be ISO-9002 and ISO 9001 certified for Quality Assurance in Production, Installation and Servicing.

        - The systems integrator shall be an authorized partner to the manufacturer and the partnership shall be at least two year old. The manufacturers - system integrator combination shall have implemented at least three projects of similar complexity in Jordan.

      - SYSTEM PERFORMANCE CRITERIA

        - In general unless otherwise mentioned elsewhere under electrical systems related detailed specifications section.

      - TRAINING

        - In general unless otherwise mentioned elsewhere under system’s related detailed specifications section, the contractor shall provide the following training for each installed system:

        - The Contractor shall provide operation, maintenance and administration training for the proposed system to Three Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and software and hardware administration of the system without or with minimal assistance from the vendor’s technical staff.

        - Engage a factory-authorized service representative, whose credentials are approved by the engineer, to explain programming and operation of systems and to train Employer's maintenance personnel on procedures and schedules for maintaining, programming, operating, and adjusting, troubleshooting, and servicing system.

        - Training shall be carried out to an approved training manual Separate training shall be provided on the hardware and software. Each training shall have both class room session and hands on session. Contractor shall allow for 6 trainees each in both the trainings.

- PRODUCTS

- Not Used

- EXECUTION

      - GENERAL

        - All Electrical Equipment and integral systems shall be commissioned in accordance with the relevant standards and regulations given in the Specification and to the recommendations of specialist Suppliers (e.g. Switchboards, Standby Generators, Fire Detection and Alarm System, Public Address System, Cables, security systems, low current systems, …etc), as well as to the Local Authorities/ Utilities acceptance; the Contractor is responsible for getting. A Report of The State Acceptance Commission which shall be part of the close out submittals the Contractor shall provide for all electrical systems.

        - Full operational tests shall be carried out on all systems to demonstrate that they operate in accordance with the requirements of the Specification.

      - CONCRETE AND FORMWORK

        - All concrete and formwork required shall be supplied and installed by the Contractor, with co-ordination and the necessary supervision by this Structural Engineer.

      - HANGERS, INSERTS, SLEEVES AND SUPPORTS

        - Provide hangers, inserts, sleeves and supports required to accommodate the equipment and materials of this Division.

        - Do not use high velocity powder activated fastenings. Low velocity powder activated fastenings may be used with the written approval of the Engineer.

        - Except for plywood backboards, do not use wood to fasten outlet boxes or electrical equipment, except where wood forms a part of the building structure at the point of installation.

        - Metal supports, screws, bolts and hardware shall be galvanized, sherardized Class 1, or stainless steel.

        - Apply cold galvanizing compound on all newly cut ferrous metal surfaces immediately after cutting.

        - Provide separate supports as required for electrical apparatus erected on or in any wall or partition. All such supporting work shall be approved by the Engineer prior to installation.

        - Do not weld to or drill building steel without the written approval of the Engineer.

        - Electrical equipment mounted against the interior surface of exterior walls shall be mounted at least 25mm away from the wall surface.

        - Electrical equipment mounted against interior walls in damp or wet locations or adjacent to liquid piping shall be mounted at least 13mm away from the surface.

        - All supports, screws and hardware in unconditioned areas i.e. car park, pump room, etc. shall be suitably primed and painted with two coats of zinc enriched paint.

      - EXCAVATION, BACKFILL, SHORING AND CONCRETE WORK

        - Excavate the last 150mm for underground ducts and conduits.

        - Backfill the first 300mm above underground ducts and conduits.

        - Refer to the Structural specification for other excavation, shoring and
backfilling work to be carried out.

        - Perform all work in accordance with the requirements of the appropriate
Divisions of this Specification.

      - CUTTING AND PATCHING

        - Perform all cutting and patching required for the work of this Division.

        - Prepare drawings showing all cutting and patching required for the installation of equipment and submit to the Engineer for approval.

        - Co-ordinate all openings with the work of other Divisions.

        - Return all surfaces to the condition encountered before the work. Acceptance of such work shall be at the discretion of the Engineer.

        - Cutting of structural members shall not be permitted without specific written approval from the Engineer. The Engineer reserves the right to dismiss from site any worker who cuts or drills structural members without specific written approval from the Engineer.

      - INSTALLATION OF ELECTRICAL EQUIPMENT

        - All work shall be executed in a workmanlike manner and shall conform to
the highest standards applicable.

        - Install equipment in accordance with the general arrangement drawings. Unless actual dimensions are indicated, take such dimensions from final reviewed shop drawings and at the site.

        - No containment shall be installed within existing concrete floors or screed toppings to floor slabs.

        - Line up exposed conduit, trunking and cable trays parallel or at right angles to building lines. Set, plumb and level equipment accurately. Install hanger rods plumb and without offsets. Install rows of fixtures accurately in line and level.

        - Flush-mount boxes, panels, cabinets and electrical devices in finished areas and provide suitable flush trims and doors or covers, unless specifically noted otherwise.

        - All areas shall be considered finished unless indicated otherwise.

        - The locations of switches, thermostats, outlets and control devices are shown diagrammatically only. Submit co-ordination drawings, which indicate in elevation the location of wiring devices. Mount switches, thermostats and other controls as close to door jambs and other openings as possible, maintaining a minimum of 100mm from trims of doors except where installed in door frames of metal partitions. Ensure that these locations meet with the approval of the Engineer. Check all doors swings and install switches on strike side of door.

        - The location of any outlet may be changed without a change to the Contract Sum, providing the relocation does not exceed 1500mm for lighting, power sockets or telephone outlets and 3000mm for motor outlets, switches or other electrical power loads.

        - Where the location of any item is shown on the architectural details or elevations, this location shall govern. No change to the Contract Sum shall be allowed for the relocation of any equipment improperly installed because of the failure to check all such details prior to the installation of the equipment. Notify the Engineer where details differ.

      - CLEANING AND PROTECTION

        - Store materials and equipment in a dry, clean place and cover with polyethylene covers as necessary.

        - Remove daily from the premises all debris, rubbish and waste material resulting from the work of this Division.

        - Clean all electrical equipment and materials before final acceptance.

        - Replace damaged, lost or stolen materials and equipment at no cost to the Owner.

        - Refinish equipment and building surfaces where damaged by the work of this Division.

        - Return all scratched surfaces to the initial condition by using original paint.

      - SYSTEM CO-ORDINATION

        - The switchgear manufacturer shall carry out a complete co-ordination study from the primary fuses or breakers including the largest fuse or breaker in each distribution panel and to select breaker trip units and fuses with characteristics to provide adequate co-ordination between all parts of the system.

        - Submit to the Engineer a complete set of manufacturer’s curves showing characteristics of tripping devices for all breakers, curves for all fuses and relays, and maximum let-through current for all ratings of fuses that have been selected. All curves shall be on standard size log-log paper.

        - Prepare on standard size log-log paper, or computer printout, a complete set of curves showing time-current characteristics of all breakers and fuses from the service overcurrent protection down to the largest devices in the 600V distribution panels, for phase and ground fault conditions. Plot the damage curves for the power transformers and cables on the same sheets. Submit three (3) sets of curves to the Engineer for approval.

        - Arrange for the manufacturer to carry out actual tests on the completed installation in the field to ensure that the required co-ordination has been provided.

      - SINGLE LINE DIAGRAM

        - Provide in each main low voltage electrical room a single line or riser diagram of the complete electrical system for the project, indicating protective and switching devices identified by type, rating and catalogue number where applicable.

        - Mount the diagram on the wall in a substantial metal frame with a glass cover accepted by Engineer.

      - OPERATION, CARE AND MAINTENANCE

        - Where required, arrange and pay for the services of the applicable manufacturers factory service engineer to supervise the initial start-up of any part of the installation, to check, adjust, balance and calibrate all components, including related wiring and controls, and to instruct the operating personnel. Provide these services for such period and for as many visits as may be necessary to put the applicable portion of the installation in complete working order, and to ensure that the operating personnel are fully conversant with all aspects of the operation, care and maintenance, all to the approval of the Engineer.

- PROVISION FOR FUTURE EXPANSION

        - In each location where a space is indicated to be reserved for future equipment, leave such space clean and install the conduit, wiring and other work pertaining to this Division in such manner that the necessary connections can be made to the future buildings, areas or equipment without dismantling existing floors, walls or ceilings. Consult with the Engineer wherever necessary for this purpose. Mark the locations of conduit terminations as directed.

      - CONTRACT DRAWINGS

        - The drawings for electrical work are diagrammatic performance drawings only, intended to convey the scope of work and indicate the general arrangement and approximate location of apparatus and fixtures, and the approximate sizes and locations of equipment and outlets. The drawings do not intend to show architectural, mechanical or structural details.

        - Do not scale or measure drawings, but obtain information regarding accurate dimensions from dimensions shown on the architectural drawings or by site measurements. Follow the electrical drawings for laying out the work.

        - Refer to the co-ordination drawings of other Divisions to become familiar with all conditions effecting the work, and verify suitable spaces exist in which the equipment is to be installed.

        - The drawings do not intend to show existing systems and/or installations. Refer to the As Built drawings and carry out site inspections to become familiar with all conditions effecting the work, and verify suitable spaces exist in which the equipment is to be installed.

      - COMPLETION OF CONTRACT

        - All equipment must be cleaned and tested before final acceptance by the Engineer.

        - From the date of issuance of the 'Completion Certificate' all equipment, materials and workmanship, other than lamps, must be unconditionally warranted for not less than one (1) year.

        - Replace, at no cost to the Owner, all incandescent lamps burned out during a thirty (30) days period, and all burned-out fluorescent and HID lamps for a period of ninety (90) days after date of issuance of 'Completion Certificate' for the Contract for the building.

        - Defects and deficiencies which originate or become evident during the warranty period, must be repaired or replaced at no cost to the Owner.

        - If, during the warranty period, transformers, ballasts or other noise and vibration producing equipment are considered by the Engineer to exceed acceptable standards, then these must be replaced without delay or additional cost to the Owner. All work relating to the replacement of defective items must be carried out after normal working hours and at a time which is acceptable to the Owner.

      - DEFINITIONS

        - Wherever the words "install", "provide", or "supply and install", are used it shall be understood to mean "provide and install, inclusive of all labor, materials, installation, commissioning, testing and connections” for the item to which it refers.

      - FIRE RATING

        - Fire Alarm and emergency lighting system wiring shall be using fire resistant cables using PVC conduits embedded in slab/wall. All surface mounted installation shall be using GI conduits.

        - Wiring for the power and control of following equipment shall be using fire resistant cables complying with BS 6387 Category CWZ: non armored cables using PVC conduits embedded in the slab/wall or GI conduits for surface mounted installation, armored cables on cable tray:

          - Circuits for life safety and Mechanical system devices required to operate in case of fire

          - Interface wiring to mechanical system such as FCU, AHU, etc. which require to be switched on or off in case of fire.

          - Branch and control circuits for smoke control and dampers.

      - MOUNTING HEIGHTS

        - Unless otherwise stated on the Drawings, the following shall be mounting heights of equipment above finished floor level subject to full coordination with architectural details, and other disciplines/equipment.  Any discrepancy found between these heights and other details/disciplines shall be brought to the notice of the Engineer for clarification and final decision.

          - Panel board	 1800 mm (Top of panel above FFL)

          - Isolating switch	 1350 mm

          - Light switch 1350 mm (100 mm from door frame, horizontally)

          - Dimmer switch 1350 mm

          - Push button station 1350 mm

          - Wall mounted telephone/intercom 1350 mm

          - Fire alarm manual call point	1350 mm

          - Fire alarm sounder 2400 mm

          - Fire alarm panel 1800 mm (Top of panel above FFL)

          - Power outlet 450 mm

          - Data/Telephone outlet 450 mm

          - TV outlet 450 mm

          - Wall mounted speaker 2100 mm

        - Where accessories with varying mounting heights (e.g. light switch and socket outlet) are shown in approximately the same location, their center lines shall be aligned vertically.

        - Where wall mounted accessories are shown adjacent to each other they shall be mounted with their wall plates separated by 50 mm.

      - PLYWOOD

        - Supply and install all marine grade plywood backboards required for the work of this Division. Plywood shall be highest quality fir, 20mm thick unless otherwise specified. Prime and paint backboards on both sides with fire retardant paint, white for general electrical, light blue for telephone/data services and orange for security services.

      - FIRE SEALS

        - Where cables, bus bars, cable tray, or conduits pass through non-fire
rated floors, walls or roof, provide internal and external sealing thereto.

        - For non-fire rated locations, sealant shall be silicone.

        - For fire rated locations, the fire stop shall meet the requirements of Authorities having jurisdiction and be to UL and BS standards with regard to the type of assembly and fire separation.

        - The Contractor shall fire seal all holes associated with the electrical equipment i.e. Cable risers, bus-bar risers, trunking / cable tray through walls etc.

      - WARNING SIGNS

        - Provide warning signs as specified to meet requirements of Authorities having jurisdiction and Engineer.

      - WIRE PULLING LUBRICANT

        - Lubricant shall be non-corrosive and approved for the type of cable used.

        - Lubricants shall be soap or wax based, depending upon application. Use soap based for short runs (not greater than 20m) and for semiconducting insulated wires, and wax based for long runs (20m or further).

      - TELECOMMUNICATIONS INTERFERENCE

        - The whole of the electrical installation work shall be so designed that there is an absolute minimum of interference with telecommunications, and the reception of broadcasting to BS 800 and any other relevant BS.

      - SEGREGATION OF SERVICES

        - The armor of all cables, cable trays, trunking, ducts etc., shall be prevented from coming into contact with non-electrical services by minimum spacing of 150mm. Where this is impracticable they shall be bonded to the exposed metal of the other services subject to the requirements contained in the IEE Regulation

      - BUILDER’S WORK

        - To reduce the necessity for cutting away and the like, certain holes and chases will be provided in the structure by the Contractor to the Consultant’s instructions. The Contractor shall plan his work so that full advantage is taken of these provision’s but it is the Contractor’s sole responsibility to ensure that all holes and chases are in the required position and that any additional ducts, holes and chases necessary for the execution of his work in the in-situ concrete walls, floor slabs, columns and beams are executed in the early stage of construction of the building.

      - MATERIALS, WORKMANSHIP AND SUPERVISION

- It is a requirement of the specification that the finished appearance of the plant in public areas is of a high architectural standard and all panels, covers, trim panels, finishes and the like shall be included to provide this required appearance to the satisfaction of the Consultant.

- The whole of the equipment supplied shall be of the best modern design and of high class durable finish and suitable for installation in a modern building which will be subjected to excessively heavy usage.

- The Contractor shall be responsible for ensuring that the components of each system are mutually compatible and integrated to form fully efficient systems complying with the Drawings and specifications.

- All materials shall be, where applicable, in accordance with the IEE Regulations, British Standards Specifications, Factories Act and Insurance Company requirements, where such exists, unless otherwise specified or agreed by the Consultant in writing.

- All articles and materials specified to conform to British Standards shall be clearly and indelibly marked and stamped with the British Standards number specified and other details required by the regulations, except where marking is impracticable when the relevant advice/delivery notes shall include the British Standard number with which they are to comply.

- All materials and workmanship shall be to the satisfaction of the Consultant, particular attention shall be paid to a neat orderly well-arranged installation, carried out in a methodical competent manner.

- The Contractor shall produce dimensional layout showing the exact location and elevation for the various outlets and shall be responsible to submit drawings/proposed material in a format to Consultant’s instruction.

- The Contractor will be required to maintain a competent supervising Engineer for the Work on site throughout the whole of the time for the completion of the Contract. The Consultant shall give prior approval to the appointment of this supervising Engineer and shall have the authority to withdraw this approval at any time.

- No person shall be allowed to execute any type of work which is normally carried out by a skilled tradesman unless he is thoroughly experienced and proficient in the trade concerned. The Consultant shall have the option to require a tradesman to demonstrate his proficiency to the satisfaction of the Consultant.

      - SAMPLES

        - The Contractor shall provide a sample properly labeled of all electrical systems devices, fittings, switches, drives, controllers, panels,etc and other like accessories described in this specification or as specified by the Consultant.

        - Such samples shall be submitted to the Consultant for his approval at his offices or elsewhere as directed, with all parts left loose, so that they may be taken apart for internal inspection by hand without the necessity of using spanners, screw drivers or wrenches.

        - It's the contractor's responsibility to get the samples approvals without any extra time extension or cost compensation.

      - STORAGE OF PLANT AND EQUIPMENT

        - All plant and equipment shall be stored off the ground under weatherproof cover until ready for incorporation in the works. All electrical apparatus shall be examined and cleaned before installation. All open conduit ends shall be fitted with plastic caps or suitable protective covering to prevent the ingress of foreign matter. All drums with cables shall be protected from direct sunlight.

      - INSPECTION AND TEST AT MANUFACTURER’S WORK

        - The Consultant shall have at all reasonable times access to the Contractor’s premises to inspect and examine the materials and workmanship of the plant and equipment during its manufacture there, and if part of the plant and equipment is being manufactured on other premises, the Contractor shall obtain for the Consultant permission to inspect as if the plant and equipment was manufactured on the Contractor’s own premises. Such inspection, examination or testing, if made, shall not relieve the Contractor from any obligation under the Contract.

        - All work, materials and the like rejected shall be corrected or replaced as necessary at the Contractor’s expense to the satisfaction of the Consultant.

        - Where the plant and equipment is a composite unit of several individual
places manufactured in different places, it shall be assembled and tested as one complete working unit. All equipment will be tested at the maker’s works to the relevant BS where applicable.

        - The aforementioned works test carried out before delivery to the Site shall not in any way relieve the Contractor of completing satisfactory site tests after erection as specified.

        - The contractor shall give the Consultant reasonable notice, at least seven clear days in writing of the date on and place at which any plant or equipment will be ready for testing as provided in the contract and the Consultant shall thereupon at his discretion notify the Contractor of his intention either to release such part of the plant and equipment upon receipt of the works tests certificates or of his intention to inspect such part of the plant and equipment and shall then, on giving twenty four hours notice in writing to the Contractor, attend at the place so named within seven days of the date by which the Contractor has stated in his notice the said plant and equipment will be ready for testing. The Contractor shall forward to the Consultant six duly certified copies of the test readings.

        - Whether at the premises of the Contractor or of any of his subcontractors, the Contractor except where otherwise specified shall provide, free of charge, such labour, materials, electricity, fuel, water, stores, apparatus and instruments as may be reasonably demanded, to carry out efficiently such tests of the plant and equipment, in accordance with the contract and shall give facilities to the Consultant to accomplish such testing.

        - Works tests shall also be carried out such that due consideration is given to the Site conditions under which the equipment is required to function. The test certifications shall give all details of such tests.

        - As and when any plant and equipment shall have passed the tests referred to in this clause the Consultant shall issue to the Contractor a notification to that effect.

        - The Contractor shall not pack for delivery or transport to site any part of the plant or equipment until he has obtained from the Consultant his written approval to the release of such part for delivery after any tests required by the Consultant in terms of this clause have been completed to his satisfaction.

- END OF SECTION