SECTION 23 0593

TESTING, ADJUSTING, AND BALANCING FOR MECHANICAL WORKS

PART 1 GENERAL

- FULL COMMISSIONING, BY AN INDEPENDENT COMMISSIONING AUTHORITY, IS A REQUIREMENT OF THIS PROJECT.

- SECTION INCLUDES

- Testing, adjustment, and balancing of air systems.

- Testing, adjustment, and balancing of all systems covered under divisions 21,22, 23 & 25.

- Measurement of final operating condition of HVAC systems.

- Sound measurement of equipment operating conditions.

- Vibration measurement of equipment operating conditions.

- Commissioning activities.

- RELATED REQUIREMENTS

- Section 01 2100 - Allowances: Inspection and testing allowances.

- Section 01 4000 - Quality Requirements: Employment of testing agency and payment for services.

- Section 01 9113 - General Commissioning Requirements: Commissioning requirements that apply to all types of work.

- Section 23 0800 - Systems Commissioning.

- REFERENCE STANDARDS

- AABC MN-1 - AABC National Standards for Total System Balance; Associated Air Balance Council; 2002.

- ASHRAE Std 111 - Measurement, Testing, Adjusting, and Balancing of Building HVAC Systems; American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc.;

2008.

- NEBB (TAB) - Procedural Standard for Testing Adjusting and Balancing of Environmental Systems; National Environmental Balancing Bureau; 2005, Seventh Edition.

- SMACNA (TAB) - HVAC Systems Testing, Adjusting, and Balancing; Sheet Metal and Air Conditioning Contractors' National Association; 2002.

- NFPA 4 Standard for Integrated Fire Protection and Life Safety System Testing; 2015.

- NFPA 25 Standard for the Inspection,Testing,and Maintenance of Water-Based Fire Protection Systems; 2015.

- International Plumbing Code; 2015.

- International Mechanical Code; 2015.

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements, for submittal procedures.

- Installer Qualifications: Submit name of adjusting and balancing agency and TAB supervisor for approval within 30 days after award of Contract.

- TAB Plan: Submit a written plan indicating the testing, adjusting, and balancing standard to be followed and the specific approach for each system and component.

- Submit to Architect/Engineer.

- Submit to the Commissioning Authority.

- Submit six weeks prior to starting the testing, adjusting, and balancing work.

- Include certification that the plan developer has reviewed the contract documents, the equipment and systems, and the control system with the Architect/Engineer and other installers to sufficiently understand the design intent for each system.

- Include at least the following in the plan:

- Preface: An explanation of the intended use of the control system.

- List of all air flow, water flow, sound level, system capacity and efficiency measurements to be performed and a description of specific test procedures, parameters, formulas to be used.

- Copy of field checkout sheets and logs to be used, listing each piece of equipment to be tested, adjusted and balanced with the data cells to be gathered for each.

- Identification and types of measurement instruments to be used and their most recent calibration date.

- Discussion of what notations and markings will be made on the duct and piping drawings during the process.

- Final test report forms to be used.

- Detailed step-by-step procedures for TAB work for each system and issue, including:

- Terminal flow calibration (for each terminal type).

- Diffuser proportioning.

- Branch/submain proportioning.

- Total flow calculations.

- Rechecking.

- Diversity issues.

- Expected problems and solutions, etc.

- Criteria for using air flow straighteners or relocating flow stations and sensors; analogous explanations for the water side.

- Details of how TOTAL flow will be determined; for example:

- Air: Sum of terminal flows via control system calibrated readings or via hood readings of all terminals, supply (SA) and return air (RA) pitot traverse, SA or RA flow stations.

- Water: Pump curves, circuit setter, flow station, ultrasonic, etc.

- Specific procedures that will ensure that both air and water side are operating at the lowest possible pressures and methods to verify this.

- Confirmation of understanding of the outside air ventilation criteria under all conditions.

- Method of verifying and setting minimum outside air flow rate will be verified and set and for what level (total building, zone, etc.).

- Method of checking building static and exhaust fan and/or relief damper capacity.

- Proposed selection points for sound measurements and sound measurement methods.

- Methods for making coil or other system plant capacity measurements, if specified.

- Time schedule for TAB work to be done in phases (by floor, etc.).

- Description of TAB work for areas to be built out later, if any.

- Time schedule for deferred or seasonal TAB work, if specified.

- False loading of systems to complete TAB work, if specified.

- Exhaust fan balancing and capacity verifications, including any required room pressure differentials.

- Interstitial cavity differential pressure measurements and calculations, if specified.

- Procedures for field technician logs of discrepancies, deficient or uncompleted work by others, contract interpretation requests and lists of completed tests (scope and frequency).

- Procedures for formal progress reports, including scope and frequency.

- Procedures for formal deficiency reports, including scope, frequency and distribution.

- Field Logs: Submit at least twice a week to the Commissioning Authority.

- Control System Coordination Reports: Communicate in writing to the controls installer all setpoint and parameter changes made or problems and discrepancies identified during TAB that affect, or could affect, the control system setup and operation.

- Progress Reports.

- Final Report: Indicate deficiencies in systems that would prevent proper testing, adjusting, and balancing of systems and equipment to achieve specified performance.

- Submit under provisions of Section 01 4000.

- Submit to the the Commissioning Authority within two weeks after completion of testing, adjusting, and balancing.

- Revise TAB plan to reflect actual procedures and submit as part of final report.

- Submit draft copies of report for review prior to final acceptance of Project. Provide final copies for Architect/Engineer and for inclusion in operating and maintenance manuals.

- Provide reports in soft cover, letter size, 3-ring binder manuals, complete with index page and indexing tabs, with cover identification at front and side. Include set of reduced drawings with air outlets and equipment identified to correspond with data sheets, and indicating thermostat locations.

- Include actual instrument list, with manufacturer name, serial number, and date of calibration.

- Form of Test Reports: Where the TAB standard being followed recommends a report format use that; otherwise, follow ASHRAE Std 111.

- Units of Measure: Report data in both I-P (inch-pound) and SI (metric) units.

- Include the following on the title page of each report:

- Name of Testing, Adjusting, and Balancing Agency.

- Address of Testing, Adjusting, and Balancing Agency.

- Telephone number of Testing, Adjusting, and Balancing Agency.

- Project name.

- Project location.

- Project Engineer.

- Project Contractor.

- Project altitude.

- Report date.

- Project Record Documents: Record actual locations of flow measuring stations and balancing valves and rough setting.

PART 2 PRODUCTS - NOT USED

PART 3 EXECUTION

- GENERAL REQUIREMENTS

- Perform total system balance in accordance with one of the following:

- AABC MN-1, AABC National Standards for Total System Balance.

- ASHRAE Std 111, Practices for Measurement, Testing, Adjusting and Balancing of Building Heating, Ventilation, Air-Conditioning, and Refrigeration Systems.

- NEBB Procedural Standards for Testing Adjusting Balancing of Environmental Systems.

- SMACNA (TAB).

- NFPA 4 Standard for Integrated Fire Protection and Life Safety System Testing.

- NFPA 25 Standard for the Inspection,Testing,and Maintenance of Water-Based Fire Protection Systems

- International Plumbing Code; 2015.

- International Mechanical Code; 2015.

- Maintain at least one copy of the standard to be used at project site at all times.

- Begin work after completion of systems to be tested, adjusted, or balanced and complete work prior to Substantial Completion of the project.

- Where HVAC systems and/or components interface with life safety systems, including fire and smoke detection, alarm, and control, coordinate scheduling and testing and inspection procedures with the authorities having jurisdiction.

- TAB Agency Qualifications:

- Company specializing in the testing, adjusting, and balancing of systems specified in this section.

- Having minimum of five years documented experience.

- Certified by one of the following:

- AABC, Associated Air Balance Council: www.aabchq.com; upon completion submit AABC National Performance Guaranty.

- NEBB, National Environmental Balancing Bureau: www.nebb.org.

- TABB, The Testing, Adjusting, and Balancing Bureau of National Energy Management Institute: www.tabbcertified.org.

- TAB Supervisor and Technician Qualifications: Certified by same organization as TAB agency.

- EXAMINATION

- Verify that systems are complete and operable before commencing work. Ensure the following conditions:

- Systems are started and operating in a safe and normal condition.

- Temperature control systems are installed complete and operable.

- Proper thermal overload protection is in place for electrical equipment.

- Final filters are clean and in place. If required, install temporary media in addition to final filters.

- Duct systems are clean of debris.

- Fans are rotating correctly.

- Fire and volume dampers are in place and open.

- Air coil fins are cleaned and combed.

- Access doors are closed and duct end caps are in place.

- Air outlets are installed and connected.

- Duct system leakage is minimized.

- Hydronic systems are flushed, filled, and vented.

- Pumps are rotating correctly.

- Proper strainer baskets are clean and in place.

- Service and balance valves are open.

- Submit field reports. Report defects and deficiencies that will or could prevent proper system balance.

- Beginning of work means acceptance of existing conditions.

- PREPARATION

- Hold a pre-balancing meeting at least one week prior to starting TAB work.

- Require attendance by all installers whose work will be tested, adjusted, or balanced.

- Provide instruments required for testing, adjusting, and balancing operations. Make instruments available to Architect/Engineer to facilitate spot checks during testing.

- Provide additional balancing devices as required.

- ADJUSTMENT TOLERANCES

- Air Handling Systems: Adjust to within plus or minus 5 percent of design for supply systems and plus or minus 10 percent of design for return and exhaust systems.

- Air Outlets and Inlets: Adjust total to within plus 10 percent and minus 5 percent of design to space. Adjust outlets and inlets in space to within plus or minus 10 percent of design.

- Hydronic Systems: Adjust to within plus or minus 10 percent of design.

- RECORDING AND ADJUSTING

- Field Logs: Maintain written logs including:

- Running log of events and issues.

- Discrepancies, deficient or uncompleted work by others.

- Contract interpretation requests.

- Lists of completed tests.

- Ensure recorded data represents actual measured or observed conditions.

- Permanently mark settings of valves, dampers, and other adjustment devices allowing settings to be restored. Set and lock memory stops.

- Mark on the drawings the locations where traverse and other critical measurements were taken and cross reference the location in the final report.

- After adjustment, take measurements to verify balance has not been disrupted or that such disruption has been rectified.

- Leave systems in proper working order, replacing belt guards, closing access doors, closing doors to electrical switch boxes, and restoring thermostats to specified settings.

- At final inspection, recheck random selections of data recorded in report. Recheck points or areas as selected and witnessed by the Employer/Owner.

- Check and adjust systems approximately six months after final acceptance and submit report.

- AIR SYSTEM PROCEDURE

- Adjust air handling and distribution systems to provide required or design supply, return, and exhaust air quantities at site altitude.

- Make air quantity measurements in ducts by Pitot tube traverse of entire cross sectional area of duct.

- Measure air quantities at air inlets and outlets.

- Adjust distribution system to obtain uniform space temperatures free from objectionable drafts and noise.

- Use volume control devices to regulate air quantities only to extend that adjustments do not create objectionable air motion or sound levels. Effect volume control by duct internal devices such as dampers and splitters.

- Vary total system air quantities by adjustment of fan speeds. Provide drive changes required. Vary branch air quantities by damper regulation.

- Provide system schematic with required and actual air quantities recorded at each outlet or inlet.

- Measure static air pressure conditions on air supply units, including filter and coil pressure drops, and total pressure across the fan. Make allowances for 50 percent loading of filters.

- Adjust outside air automatic dampers, outside air, return air, and exhaust dampers for design conditions.

- Measure temperature conditions across outside air, return air, and exhaust dampers to check leakage.

- Where modulating dampers are provided, take measurements and balance at extreme conditions. Balance variable volume systems at maximum air flow rate, full cooling, and at minimum air flow rate, full heating.

- Measure building static pressure and adjust supply, return, and exhaust air systems to provide required relationship between each to maintain approximately 12.5 Pa (0.05 inches) positive static pressure near the building entries.

- Check multi-zone units for motorized damper leakage. Adjust air quantities with mixing dampers set first for cooling, then heating, then modulating.

- For variable air volume system powered units set volume controller to air flow setting indicated. Confirm connections properly made and confirm proper operation for automatic variable air volume temperature control.

- COMMISSIONING

- See Sections 01 9113 and 23 0800 for additional requirements.

- Perform prerequisites prior to starting commissioning activities.

- Fill out Prefunctional Checklists for all systems listed in 3.09 below.

- Furnish to the Commissioning Authority, upon request, any data gathered but not shown in the final TAB report.

- Re-check minimum outdoor air intake flows and maximum and intermediate total airflow rates

For 10 percent of the air handlers plus a random sample equivalent to 50 percent of the final

TAB report data as directed by Commissioning Authority.

- Original TAB agency shall execute the re-checks, witnessed by the Commissioning Authority.

- Use the same test instruments as used in the original TAB work.

- Failure of more than 10 percent of the re-checked items of a given system shall result in the rejection of the system TAB report; rebalance the system, provide a new system TAB report, and repeat random re-checks.

- For purposes of re-check, failure is defined as follows:

- Air Flow of Supply and Return: Deviation of more than 10 percent of instrument reading.

- Minimum Outside Air Flow: Deviation of more than 20 percent of instrument reading; for inlet vane or VFD OSA compensation system using linear proportional control, deviation of more than 30 percent at intermediate supply flow.

- Temperatures: Deviation of more than 0.5 degree C (one degree F).

- Air and Water Pressures: Deviation of more than 10 percent of full scale of test instrument reading.

- Sound Pressures: Deviation of more than 3 decibels, with consideration for variations in background noise.

- For purposes of re-check, a whole system is defined as one in which inaccuracies will have little or no impact on connected systems; for example, the air distribution system served by one air handler or the hydronic chilled water supply system served by a chiller or the condenser water system.

- In the presence of the Commissioning Authority, verify that:

- Final settings of all valves, splitters, dampers and other adjustment devices have been permanently marked.

- The air system is being controlled to the lowest possible static pressure while still meeting design loads, less diversity; this shall include a review of TAB methods, established control setpoints, and physical verification of at least one leg from fan to diffuser having all balancing dampers wide open and that during full cooling of all terminal units taking off downstream of the static pressure sensor, the terminal unit on the critical leg has its damper 90 percent or more open.

- The water system is being controlled to the lowest possible pressure while still meeting design loads, less diversity; this shall include a review of TAB methods, established control setpoints, and physical verification of at least one leg from the pump to the coil having all balancing valves wide open and that during full cooling the cooling coil valve of that leg is 90 percent or more open.

- Any tests with deemed inconclusive, inconsistent or unsatisfactory by the Engineer, Employer or Commissioning Agent shall be repeated at their discretion time of choosing.

- Performance tests for HVAC system shall be performed at the completion of the systems and during hottest and most humid month of the year regardless of the completion date of the system. Test during hottest most humid month can be carried out during defects liability period. The date of such test must be determind in coordination with the Engineer and Commissioning Authority. The Contractor shall write one week in advance advising that the weather forecast anticipate rise in temperature and humidity and request approval to perform test in the proposed date.

- SCOPE

- Test, adjust, and balance the following:

- Fire Pumps.

- Plumbing Pumps.

- Water treatment equipment

- .Unit Air Conditioners.

- Air Handling Units.

- Fans.

- Air Filters.

- Air Terminal Units.

- Air Inlets and Outlets.

- Controls Compressor.

In addition to any applicable mechanical equipment in the project other mentioned above.

- MINIMUM DATA TO BE REPORTED (EMPLOYER, ENGINEER OR COMMISSIONING AUTHORITY MAY REQUIRE FURTHER DATA):

- Room by room during hottest month of the year:

- Ambient dry bulb temperature

- Ambient wet bulb temperature

- Room dry bulb temperature

- Room relative humidity

- Room octave bands

- Electric Motors:

- Manufacturer.

- Model/Frame.

- HP/BHP.

- Phase, voltage, amperage; nameplate, actual, no load.

- RPM.

- Service factor.

- Starter size, rating, heater elements.

- Sheave Make/Size/Bore.

- V-Belt Drives:

- Identification/location.

- Required driven RPM.

- Driven sheave, diameter and RPM.

- Belt, size and quantity.

- Motor sheave diameter and RPM.

- Center to center distance, maximum, minimum, and actual.

- Pumps:

- Identification/number.

- Manufacturer.

- Size/model.

- Impeller.

- Service.

- Design flow rate, pressure drop, BHP.

- Actual flow rate, pressure drop, BHP.

- Discharge pressure.

- Suction pressure.

- Total operating head pressure.

- Shut off, discharge and suction pressures.

- Shut off, total head pressure.

- Cooling Coils:

- Identification/number.

- Location.

- Service.

- Manufacturer.

- Air flow, design and actual.

- Entering air DB temperature, design and actual.

- Entering air WB temperature, design and actual.

- Leaving air DB temperature, design and actual.

- Leaving air WB temperature, design and actual.

- Air pressure drop, design and actual.

- Air Moving Equipment:

- Location.

- Manufacturer.

- Model number.

- Serial number.

- Arrangement/Class/Discharge.

- Air flow, specified and actual.

- Return air flow, specified and actual.

- Outside air flow, specified and actual.

- Total static pressure (total external), specified and actual.

- Inlet pressure.

- Discharge pressure.

- Sheave Make/Size/Bore.

- Number of Belts/Make/Size.

- Fan RPM.

- Return Air/Outside Air:

- Identification/location.

- Design air flow.

- Actual air flow.

- Design return air flow.

- Actual return air flow.

- Design outside air flow.

- Actual outside air flow.

- Return air temperature.

- Outside air temperature.

- Required mixed air temperature.

- Actual mixed air temperature.

- Design outside/return air ratio.

- Actual outside/return air ratio.

- Exhaust Fans:

- Location.

- Manufacturer.

- Model number.

- Serial number.

- Air flow, specified and actual.

- Total static pressure (total external), specified and actual.

- Inlet pressure.

- Discharge pressure.

- Sheave Make/Size/Bore.

- Number of Belts/Make/Size.

- Fan RPM.

- Duct Traverses:

- System zone/branch.

- Duct size.

- Area.

- Design velocity.

- Design air flow.

- Test velocity.

- Test air flow.

- Duct static pressure.

- Air temperature.

- Air correction factor.

- Duct Leak Tests:

- Description of ductwork under test.

- Duct design operating pressure.

- Duct design test static pressure.

- Duct capacity, air flow.

- Maximum allowable leakage duct capacity times leak factor.

- Test apparatus:

- Blower.

- Orifice, tube size.

- Orifice size.

- Calibrated.

- Test static pressure.

- Test orifice differential pressure.

- Leakage.

- Air Monitoring Stations:

- Identification/location.

- System.

- Size.

- Area.

- Design velocity.

- Design air flow.

- Test velocity.

- Test air flow.

- Flow Measuring Stations:

- Identification/number.

- Location.

- Size.

- Manufacturer.

- Model number.

- Serial number.

- Design Flow rate.

- Design pressure drop.

- Actual/final pressure drop.

- Actual/final flow rate.

- Station calibrated setting.

- Air Distribution Tests:

- Air terminal number.

- Room number/location.

- Terminal type.

- Terminal size.

- Area factor.

- Design velocity.

- Design air flow.

- Test (final) velocity.

- Test (final) air flow.

- Percent of design air flow.

- Sound Level Reports:

- Location.

- Octave bands - equipment off.

- Octave bands - equipment on.

- Vibration Tests:

- Location of points:

- Fan bearing, drive end.

- Fan bearing, opposite end.

- Motor bearing,	center	(if applicable).

- Motor bearing,	drive end.

- Motor bearing, opposite end.

- Casing (bottom or top).

- Casing (side).

- Duct after flexible connection (discharge).

- Duct after flexible connection (suction).

- Test readings:

- Horizontal, velocity and displacement.

- Vertical, velocity and displacement.

- Axial, velocity and displacement.

- Normally acceptable readings, velocity and acceleration.

- Unusual conditions at time of test.

- Vibration source (if non-complying).

END OF SECTION