- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Section includes electrical connections to equipment.

      - REFERENCES

        - BS 7655	Specification for PVC Insulated Cables (non-armored).

        - BS 6121	Mechanical Cable Glands (Specifications for).

        - BS 6500	Specification for Insulated Flexible Cords and Cables.

        - BS 6746	Specification for PVC Insulation and Sheath of Electric Cables.

        - BS 7671 Requirements for Electrical Installations (IEE Wiring Regulations, 17th Edition) with all current additions and amendments.

        - Local Codes and Regulations.

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

        - Provide samples of all proposed equipment wiring connections, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Provide method statement for installation, testing and commissioning of equipment wiring connections.

        - Product Data: Submit wiring device manufacturer’s catalog information showing dimensions, configurations, and construction.

        - Manufacturer's installation instructions.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations, sizes, and configurations of equipment connections.

      - COORDINATION

        - Obtain and review shop drawings, product data, manufacturer’s wiring diagrams, and manufacturer's instructions for equipment furnished under other sections.

        - Determine connection locations and requirements.

        - Sequence rough-in of electrical connections to coordinate with installation of equipment.

        - Sequence electrical connections to coordinate with start-up of equipment.

      - QUALIFICATIONS

        - Manufacturers: Firms regularly engaged in manufacture of Equipment wiring connections of types and ratings required, whose products have been in satisfactory use in similar service for not less than 10 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - QUALITY ASSURANCE

        - Wiring connections shall generally be manufacturer’s standard construction and materials.

        - All wring connections and accessories furnished under these Specifications shall conform to the applicable standards, IEE, IEC and BS.

      - DELIVERY, STORAGE AND HANDLING

        - Store Pack all wiring accessories for protection during transportation.

        - Store wiring connections in an appropriate protection against corrosion and damage.

        - Do not install wiring connections and accessories until it can be protected from damage during construction.

      - SPARE PARTS

        - Supply as maintenance stock, additional devices of all types and ratings, amounting to one unit for every 10 installed units, but not less than two units of each type and rating.

        - Incase three or less numbers of any device of certain rating/ size are installed, a minimum of one for each three numbers additional devices of same rating/ size shall be provided as spare.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - CABLE TYPES

        - Cables shall be utilized as detailed in Section 26 05 19.

      - LOW VOLTAGE CABLE AND WIRING (SUPPORT SYSTEMS)

        - Support all cables and wiring throughout their length as detailed in sections 26 05 19, 26 05 33 and 26 05 29.

      - WIRING

        - Wiring cables shall be utilized as detailed in section 26 05 19, 26 27 26, 21 05 13 and 26 24 19.

      - CONNECTIONS

        - Each equipment connection shall be provided with complete assembly of material, including but not necessary limited to, pressure connectors, terminals, lugs, electrical insulating tape, electrical solder, electrical soldering flux, heat-shrinkable insulating tubing, cable ties, solder less wire nuts, and other items and accessories as needed to complete splices and terminations of wires and cables.

        - Heavy gauge PVC and G.I metal conduits and fittings of the required types, grades, sizes and thickness, for each type of electrical equipment connection shall be provided. Where types and grades are not indicated, provide proper selection to comply with wiring and raceway requirements. Provide products complying with section 26 27 26 and in accordance with the following listing of conduit and fittings.

          - Heavy gauge PVC conduit and fittings (for indoor except plant rooms).

          - PVC coated rigid steel conduit and fittings (for outdoor, wet areas and plant rooms).

          - Rigid steel metal conduit and fittings.

          - PVC coated electrical metallic tubing and fittings.

          - Flexible metal conduit and fittings (for indoor except plant rooms and wet areas).

          - Liquid-tight flexible metal conduit and fittings (for outdoor, wet areas and plant rooms).

        - Electrical connectors, lugs and terminals for the wires and cables shall be provided as recommended by the connector and terminal manufacturer for intended applications.

        - Equipment connection accessories such as electrical insulating tape, heat-shrinkable insulating tubing and boots, solder, electrical soldering flux, wire nuts, cable ties, etc. shall be provided as recommended by accessories manufacturers for the intended applications and as approved by the Engineer.

        - For remote monitoring/controls of the electrical connections to various equipment, comply with the requirements of divisions 22 and 23.

- EXECUTION

      - GENERAL

        - A.	All clauses as detailed in section 26 05 19, 26 27 26 and 26 24 19.

      - EXAMINATION

        - A.	Verify equipment is ready for electrical connection, for wiring, and to be energized.

      - INSTALLATION

        - Make electrical connections.

        - Make conduit connections to equipment using flexible conduit. Use liquid tight flexible conduit with watertight connectors in damp or wet locations.

        - Connect heat producing equipment using wire and cable with insulation suitable for temperatures encountered.

        - Install receptacle outlet to accommodate connection with attachment plug.

        - Install cord and cap for field-supplied attachment plug.

        - Install suitable strain-relief clamps and fittings for cord connections at outlet boxes and equipment connection boxes.

        - Install disconnect switches, controllers, control stations, and control devices to complete equipment wiring requirements.

        - Install terminal block jumpers to complete equipment wiring requirements.

        - Install interconnecting conduit and wiring between devices and equipment to complete equipment wiring requirements.

      - ADJUSTING

        - Cooperate with utilization equipment installers and field service personnel during checkout and starting of equipment to allow testing and balancing and other startup operations.

        - Provide personnel to operate electrical system and checkout wiring connection components and configurations.

- END OF SECTION