SECTION 221123 - PLUMBING PUMPS

PART 1 GENERAL

- SUMMARY

- General

- Read this Section in conjunction with other related Sections, the General Requirements, the Design Drawings and the Contract Conditions.

- Performance Specified Work

- Refer to the Contractor's Responsibilities in the General Requirements for specific requirements.

- Supply, deliver, install and warrant the work in strict compliance with the materials and workmanship requirements of the Specification.

- Where required to prepare Shop Drawings, these shall be limited to final detailing of components, systems indicated on the Design Drawings, necessary to demonstrate their safe installation.

- Where products are offered by the Contractor for acceptance by the Engineer, provide full supporting documentation in respect of the complete system or installation.

- Included Systems/ Products

- Plumbing Pumps.

- SUBMITTALS

- General: Comply with the requirements of the General Requirements and submit the following.

- Post Contract Submittals

- Shop Drawings.

- Product Data on materials and components for use.

- Supplementary Product Literature: Include a statement from the manufacturer for the design life of the system.

- List of tests included.

- Certified test data.

- Outline technical specifications reflecting proposed materials and systems.

- A list of proposed suppliers and Subcontractors intended to be used.

- Method Statement.

- Quality Plan.

- Summary of deviations from the Specification.

- CLOSEOUT SUBMITTALS

- General: Comply with the requirements of the General Requirements and submit the following.

- Warranties.

- Operation and Maintenance (O&M) Manuals: Include component list with manufacturer's reference numbers, descriptions of materials and procedures for repairing and cleaning of finishes and cleaning frequency.

- Recommended Spare Parts List: Turn over to the Employer prior to issuance of the Taking-Over Certificate, the manufacturer's recommended spare part list for 2 years of continuous operation.

- QUALITY ASSURANCE

- Acceptable Manufacturer

- The manufacturer shall have at least 10 years of experience in the design and manufacture of plumbing pumps.

- Pump Selection

- Head capacity curves shall slope up to maximum head at shut off. Curves shall be relatively flat for closed systems. Select pumps near the midrange of the curve, so that the design capacity falls to the left of the best efficiency point, to allow a cushion for the usual drift to the right in operation, without approaching the pump curve end point and possible cavitation and unstable operation.

- Select pumps for open systems so that required net positive suction head (NPSHR) does not exceed the net positive head available (NPSHA). Deviations within 3% of maximum efficiency shall be permissible, provided the lesser efficiency shall not less than the scheduled efficiency.

- Operating point of flow and head shall fall near point of maximum efficiency obtained from manufacturer's published data. Do not select pumps to operate near the end of their curve.

- Standards: In addition to the requirements indicated on the Design Drawings, or specified in the General Requirements and Specification, the Work shall be in accordance with the following standards, codes and relevant statutory requirements.

- Uniform Plumbing Code (UPC).

- International Plumbing Code (IPC).

- American Society for Testing and Materials, ASTM International Standards.

- BSI Group, (BS) British Standards.

- National Electrical Manufacturers Association, NEMA Standards.

- Provide testing and inspections in accordance with the General Requirements.

- Preconstruction Testing/ Reports

- Submit reports of independent tests demonstrating that the products and systems are in accordance with the indicated performance requirements.

- Where test results for a material or product are not available, undertake testing to show compliance with the Specification at an independent testing laboratory acceptable to the Engineer.

- The provision of testing data or the carrying-out of tests does not relieve the Contractor of his responsibilities regarding the performance requirements, durability or service life requirements.

PART 2 PRODUCTS

- SYSTEMS/ PRODUCTS

- Booster Pumps

- Description: Booster pumps for domestic water supply system, comprising the following components and installed to locations indicated on the Design Drawings. Include pressure vessels, controls and all necessary accessories to complete the installation. Booster pumps shall run to distribute water at a required system pressure as indicated on the Design Drawings.

- Pump

- Booster pumps shall be of Transfer pumps shall be of end-suction or vertical multistage centrifugal construction as indicated on the Design Drawings

- Pumps shall be provided with stainless steel base and head, and parts in contact with the liquid shall be stainless steel 316 including casing, shafts and impellers. Pumps shall be provided with tungsten carbide faced mechanical seals. Pumps shall be capable of providing the required performance described above and in the pump duties clause with a minimum efficiency of 66%. They shall be capable of operating with a reasonable total head to closed valve head ratio

- Motor

a) The motor shall be of a constant or variable speed totally enclosed fan-cooled (TEFC) type and 2-pole standard motor.

- Transfer Pumps

- Description: Transfer pumps for domestic water supply system, comprising the following components and installed to locations indicated on the Design Drawings. Include all necessary accessories to complete the installation. Transfer pumps shall run to distribute water from one tank to another as indicated on the Design Drawings.

- Pump

- Transfer pumps shall be of end-suction or vertical multistage centrifugal construction as indicated on the Design Drawings.

- Pumps shall be provided with stainless steel base and head, and parts in contact with the liquid shall be stainless steel 316 including casing, shafts and impellers. Pumps shall be provided with tungsten carbide faced mechanical seals. Pumps shall be capable of providing the required performance described above and in the pump duties clause with a minimum efficiency of 66%. They shall be capable of operating with a reasonable total head to closed valve head ratio

- Motor

- The motor shall be of a constant speed totally enclosed fan-cooled (TEFC) type and 2-pole standard motor.

- Submersible Sump Pumps

For spec. refer to BOQ.

- IN-LINE CIRCULATOR PUMPS

- Casing: Bronze, rated for 860 kPa (125 psig) working pressure, with stainless steel rotor assembly.

- Impeller: Bronze.

- Shaft: Alloy steel with integral thrust collar and two oil lubricated bronze sleeve bearings.

- Seal: Carbon rotating against a stationary ceramic seat.

- Drive: Flexible coupling.

- DESIGN CRITERIA

- General

- Plumbing pumps shall be of duty and standby configuration as indicated on the Design Drawings.

- The size, capacity and model of pumps shall be selected based on the system flow requirements as indicated on the Design Drawings.

- Stainless steel pump components shall be of Grade 304/ 316 to suit the potable water supply requirements.

- Connections

- Pump inlet and outlet connections shall be of diameters indicated on the Design Drawings.

- Pump inlet and outlet connections shall be flanged type and shall match the pipe configurations indicated on the Design Drawings.

- Electrical supply and connection requirements shall be as indicated on the Design Drawings.

- Motor

- The motor shall be fabricated in accordance with IEC 60034.

- The motor shall have Class F insulation and Class B temperature rise in accordance with NEMA Standards.

- Base Plate and Foundation

- Pump and motor shall be mounted on a common base plate.

- The base plate shall be mechanically fixed to the supporting substrate; mechanical fixings shall be in accordance with pump manufacturer's recommendations.

- Lifting points shall be secured to the base plate and enable the pump unit to be moved without causing damage to any components. Provide a metal coupling guard.

- The base plate shall be securely attached to a solid foundation in such a way that pump and motor shaft alignment is ensured.

- The foundation shall be sufficiently substantial to form a permanent and rigid support for the base plate.

- PERFORMANCE REQUIREMENTS

- Flow Rate and Head

1. The pump flow rate and head shall be as indicated on the Design Drawings.

- Power

1. The motor rating and electrical power supply requirements shall be as indicated on the Design Drawings.

- MATERIALS

A.	Pump Components

- Stainless steel impellers and shafts shall be in accordance with ASTM A276 or acceptable BS/ EN Standard.

- Cast iron housing shall be in accordance with BS EN 1561.

- Steel base plates shall be in accordance with BS EN 10025.

- SOURCE QUALITY CONTROL

- General

- Pumps shall be factory tested in accordance with the requirements of BS EN ISO 9906.

- Tests certificates shall be provided for review and acceptance of the Engineer prior to shipment.

- Factory Testing

1. The following pump parameters shall be measured during factory testing:

- Flow rates.

- Total head.

- Motor power input.

- Nominal speed.

PART 3 EXECUTION

- EXAMINATION

A. Verification of Conditions

1. Examine areas for compliance with requirements for installation and conditions affecting performance of the Work. Identify conditions detrimental to a proper and timely completion. Proceed with installation only after unsatisfactory conditions have been corrected.

- INSTALLATION

A. General

- Install pumps in accordance with the manufacturer's recommendations.

- Install pumps with access for periodic service and maintenance including removal of motors, impellers, couplings and accessories.

- Fabricate brackets or supports as required. Install pumps with motor and pump shafts vertical. Use continuous-thread hanger rods and spring hangers with vertical-limit stop of sufficient size to support pump weight.

- Install piping adjacent to machine to allow service and maintenance.

- Install pressure gages on pump suction and discharge, at integral pressure gage tapping or install single gage with multiple input selector valve.

- Install electrical connections for power, controls and devices.

- SITE QUALITY CONTROL

A. Inspection and Testing

- The Contractor shall notify the Engineer of the time at which all tests shall be held and shall provide all the materials, labor and equipment required for testing. Upon completion of the test, copies of the complete records shall be given to the Engineer for his retention in accordance with applicable Divisions of Specification.

- The Contractor shall ensure the safety of the pipework under test and he shall be responsible for the pipework and ancillary work during the test and shall replace or repair as directed by the Engineer, any pipe or fitting, which in the opinion of the Engineer has failed to withstand the test.

- Booster Pump

- Run booster pump to ascertain available pressure at highest point in the building with maximum flow from all pumps operating.

- Check Pump Alternator.

- DEMONSTRATION AND TRAINING

A. Demonstration

1. Demonstrate to the Engineer, the features and functions of the system and subsystems, including the labeling process.

2. Furnish the necessary trained personnel to perform the demonstration and instructions and arrange to have the manufacturer's representatives present to assist with the demonstrations.

B. Training

- Instruct the Employer and designated representatives in the proper operation and maintenance of the system.

- Conduct a training course for members of the operating and maintenance staff as designated by the Engineer

- The training course shall be given at the installation during normal working hours and shall start after the system is functionally complete but prior to final acceptance tests

END OF SECTION