SECTION 23 3700
AIR OUTLETS AND INLETS

| PART 1 | GENERAL |
| --- | --- |
| 1.01 SECTION INCLUDES |  |
| A. | Diffusers. |
| B. | Light troffer diffusers |
| C. | Registers/grilles. |
| D. | Door grilles. |
| E. | Louvers. |
| F. | Goosenecks. |

- RELATED REQUIREMENTS

- Section 09 9123 - Interior Painting: Painting of ducts visible behind outlets and inlets.

- REFERENCE STANDARDS

- AMCA 500-L - Laboratory Methods of Testing Louvers for Rating; Air Movement and Control Association International, Inc.; 2012.

- ASHRAE Std 70 - Method of Testing the Performance of Air Outlets and Inlets; American Society of Heating, Refrigerating and Air Conditioning Engineers, Inc.; 2006 (R2011).

- SMACNA (DCS) - HVAC Duct Construction Standards Metal and Flexible; Sheet Metal and Air Conditioning Contractors' National Association; 2005.

- SUBMITTALS

- See Section 01 3000 - Administrative Requirements for submittal procedures.

- Product Data: Provide data for equipment required for this project. Review outlets and inlets as to size, finish, and type of mounting prior to submission. Submit schedule of outlets and inlets showing type, size, location, application, and noise level.

- Samples: Submit two of each required air outlet and inlet type.

- Project Record Documents: Record actual locations of air outlets and inlets.

- QUALITY ASSURANCE

- Test and rate air outlet and inlet performance in accordance with ASHRAE Std 70.

- Test and rate louver performance in accordance with AMCA 500-L.

- QUALITY ASSURANCE

- Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum ten years of documented experience.

- MOCK-UP

- Provide mock-up of typical exterior ceiling module with supply and return air outlets.

- Locate where directed.

- Mock-up may remain as part of the Work.

PART 2 PRODUCTS

- RECTANGULAR CEILING DIFFUSERS

- Type: Provide square, stamped, multi-core diffuser to discharge air in 360 degree, one way, two way, three way, and four way pattern with sectorizing baffles where indicated.

- Connections: As scheduled on drawings.

- Frame: Provide surface mount type. In plaster ceilings, provide plaster frame and ceiling frame.

- Fabrication: Aluminum with powder coat finish.

- Color: standard color matching ceiling.

- Accessories: Provide radial opposed blade volume control damper; removable core with damper adjustable from diffuser face.

- PERFORATED FACE CEILING DIFFUSERS

- Type: Perforated face with fully adjustable pattern and removable face.

- Frame: Surface mount type. In plaster ceilings, provide plaster frame and ceiling frame.

- Fabrication: Steel with aluminum frame and baked enamel finish.

- Color: standard color matching ceiling.

- CEILING LINEAR SLOT DIFFUSERS

- Type: Continuous slot width as scheduled on drawings number of slots as

scheduled on drawings, with adjustable vanes for left, right, or vertical discharge.

- Fabrication: Aluminum extrusions with factory powder coated finish.

- Color: standard color matching ceiling.

- Frame: 32 mm (1-1/4 inch) margin with concealed mounting and gasket, mitered end border.

- Plenum: Integral, galvanized steel, insulated.

- CEILING SUPPLY REGISTERS/GRILLES

- Type: Streamlined and individually adjustable curved blades to discharge air along face of grille, two-way deflection.

- Frame: 32 mm (1-1/4 inch) margin with concealed mounting and gasket.

- Construction: Made of aluminum extrusions with factory powder coated finish.

- Color: standard color matching ceiling.

- Damper: Integral, gang-operated, opposed blade type with removable key operator, operable from face.

- CEILING EXHAUST AND RETURN REGISTERS/GRILLES

- Type: Continuous slot width as scheduled on drawings, number of slots as scheduled on drawings, with adjustable vanes for left, right, or vertical discharge.

- Frame: 32 mm (1-1/4 inch) margin with concealed mounting.

- Construction: Made of aluminum extrusions with factory powder coated finish.

- Color: standard color matching ceiling.

- WALL SUPPLY REGISTERS/GRILLES

- Type: Streamlined and individually adjustable blades, 3/4 inch (19 mm) minimum depth, 3/4 inch (19 mm) maximum spacing with spring or other device to set blades, vertical face, double deflection.

- Frame: 32 mm (1-1/4 inch) margin with concealed mounting and gasket.

- Fabrication: Made of aluminum extrusions with factory powder coated finish.

- Color: standard color matching wall.

- Damper: Integral, gang-operated opposed blade type with removable key operator, operable from face.

- WALL EXHAUST AND RETURN REGISTERS/GRILLES

- Type: Streamlined blades, 19 mm (3/4 inch) minimum depth, 19 mm (3/4 inch) maximum spacing, with spring or other device to set blades, vertical face.

- Frame: 32 mm (1-1/4 inch) margin with countersunk screw mounting.

- Fabrication: Aluminum extrusions, with factory powder coated finish.

- Color: standard color matching wall.

- DOOR GRILLES

- Type: V-shaped louvers of 0.91 mm (20 gage, 0.0359 inch) thick steel, 25 mm (1 inch) deep on 13 mm (1/2 inch) centers.

- Frame: 0.91 mm (20 gage, 0.0359 inch) steel with auxiliary frame to give finished appearance on both sides of door, with factory prime coat finish.

- LOUVERS

- Intake Air Louvers: 100 mm (4 inch) deep with blades on 45 degree slope with center baffle and return bend, heavy channel frame, 13 mm (1/2 inch) square mesh screen over exhaust and 13 mm (1/2 inch) square mesh screen over intake.

- Fresh air louvers shall be supplied with aluminum washable filters. Filters shall be housed in a heavy duty frame that permits easy removal.

- Exhaust Air Louvers: Gravity Shutter Type or as indicated on drawings

- Fabrication: 1.52 mm (16 gage, 0.0598 inch) thick extruded aluminum assembly, with factory anodized finish.

- Color: standard color matching wall.

- GOOSENECKS

A. Fabricate in accordance with SMACNA (DCS) of minimum 1.21 mm (18 gage, 0.0598 inch) galvanized steel.

PART 3 EXECUTION

3.01 INSTALLATION

- Install in accordance with manufacturer's instructions.

- Check location of outlets and inlets and make necessary adjustments in position to conform with architectural features, symmetry, and lighting arrangement.

- Install diffusers to ductwork with air tight connection.

- Paint ductwork visible behind air outlets and inlets matte black. Refer to Section 09 9123

- The air terminal devices shall be identified by reference number as to their final location.

Plenum boxes shall be similarly numbered to reduce the risk of incorrect matching.

- Grilles, diffusers and plenum boxes shall be supported independently from the building structure unless otherwise instructed by the Engineer. Grilles diffusers and plenums shall not be supported from the ceiling grid.

- Diffusers shall be securely fixed to plenum boxes by means of concealed adjustable mounting brackets.

- During construction the Contractor shall ensure that the location and fixing of all grilles and diffusers is fully coordinated between the relevant trades.

END OF SECTION