- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Wiring Devices used as accessories for the Electrical Installations including, but not limited to the following:

            - Indoor lighting switches.

            - outdoor lighting switches.

            - Socket outlets.

            - Industrial socket outlets.

            - Isolators.

            - Spur or fused connection units.

            - Outlets for low current systems.

      - REFERENCES

        - BS EN 60669 Part 1: 2000 Switches for Domestic and Other Purposes

        - BS 1363: 1995 13A Fused Plugs Switched and Unswitched Socket Outlets and Boxes

        - BS EN 60670-22: 2006 General Requirements for Electrical Accessories

        - BS EN 60947-3: Low voltage switchgear and control gear. Switches, disconnectors, switch-disconnectors and fuse- combination units.

        - BS 546:	Two Pole and Earthing Pin Plugs, Socket Outlets.

        - BS 6972 & BS 5733: Ceiling Roses

        - BS EN 60529:1992

        - Requirements of Public Authority for Electricity and Water (PAEW) Regulations.

        - Requirements For Electrical Installations, (IEE 17th Wiring Regulations) With All Current Additions and Amendments where do not contradict PAEW Regulations.

        - DIN 49440/49441

        - Local Codes, Standards and Regulations.

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating to the wiring devices proposed, which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

        - Provide samples of all proposed devices, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Method Statement for system installation, wiring, testing, operation and commissioning.

      - QUALIFICATIONS

        - Manufacturers: Firms regularly engaged in manufacture of wiring devices of types and ratings required, and whose products have been in satisfactory use in similar service for not less than 5 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation and experience on projects with Wiring Devices similar to that required for this project.

      - QUALITY ASSURANCE

        - Wiring devices shall comply with the applicable standards of Local Standards Organization and BS. Power outlets shall comply with CEE 7/4, DIN 49440/49441

        - Any defects or damage caused partly or wholly in the installation of wiring devices to the building or building fabric shall be made good to the satisfaction of the Engineer.

      - DELIVERY, STORAGE AND HANDLING

        - All wiring devices shall be delivered in factory pack wrapping and boxes and stored in a clean, dry space within the racks.

      - EXTRA MATERIALS / SPARE PARTS FOR OPEARTION AND MAINTENANCE

        - Provide 5 % of each style, size and finish wall plates with accessories but no fewer than 5 of each.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Contractor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - Lighting switches shall conform to B.S 3676 Part 1: 1989 & EN 60669-1.

        - For single and multi-gang units in general locations with surface installation work light switches shall be metal clad.

        - Switch plates, socket-outlet plates and similar items for back of house areas shall be of white plastic type for recessed installations and to the approval of the Engineer.

        - Sockets and switches in public areas, rooms,….etc. shall be with decorative face plate as per ID.  If sockets are hidden by furniture it may be non-decorative standard based on the ID drawings and approval.

        - Decorative finishes of metal plates shall comply with appropriate standards, as mentioned elsewhere. The finish and/or color shall be standard throughout the installation unless otherwise indicated or as directed by the Engineer.

        - Switches shall comply with reference standards and be suitable for use on inductive and resistive loads. They shall be single pole for 1-phase and neutral supply and double pole for 2-phase supply, unless otherwise indicated or directed by the Engineer. Where switches are mounted adjacent one to another, they shall be grouped in a single enclosure and share a common switch plate.

        - Where indicated, switches with pilot lamps shall be provided. This lamp shall be a 6 Watt neon lamp with resistor and red colored lens unless otherwise indicated.

        - Plugs from the same manufacturer as that of the socket outlets shall be provided with all types of socket-outlets, and handed over to the Engineer.

        - All the materials used in the manufacture and installation of disconnect switches, push button stations, isolators and mains power isolation shall be of high quality and of proven suitability for the functions they will perform and the conditions they will meet in service. Each of these items shall be the product, manufacture and assembly of one manufacturer only.

        - For remote monitoring/controls, comply with the requirements as given in Section 25 50 00.

        - For switches and receptacles, metal boxes shall be used, which shall be connected to earth continuity conductor of the circuit.

        - Grid switches shall be equipped with phase barriers where different phases are connected to the grid switch.

      - WIRING DEVICES FINISHING

        - Refer to Interior Design finishes for all front of house and public areas.

        - White PVC molded finish - flush mounted in back of house areas other than plant rooms, wet or external areas.

        - Steel cover plate, zinc phosphated and polyester coated finish for surface installation in plant rooms.

        - Impact resistant, weatherproof accessories with polycarbonate housing and IP56 protection rating for wet or external areas.

        - All devices of one particular type shall be of the same range from a single manufacturer.

      - INDOOR LIGHTING SWITCHES

        - Lighting switches shall conform to B.S3676 Part 1: 1989 & EN 60669-1.

        - Lighting switches for interior use, shall be heavy duty, AC, single or double pole, minimum 10A with number of ways as shown on the Drawings and mounted on adjustable grid enclosed in metal box. The switches shall be of the quick make, slow break type and shall be capable of switching 100 % rated load of the types shown on the Drawings.

        - Where switches are to be flush type they shall be supplied with overlapping cover plates finished flush with the sides of the metal box.

      - OUTDOOR LIGHTING SWITCHES

        - All outdoor lighting switches shall have the characteristics as described above for indoor lighting switches, but be complete with a gasket forming splash proof and dustproof enclosures.

        - Waterproof switches and enclosure shall comply with BS 3676: Part 1:1989 and protected to IP56 according to BS EN 60529:1992, construction of enclosures shall be from extremely robust polycarbonate sailed against dust & water & impact resistant

        - A suitable drain hole shall be provided.

      - 13 AMPERE SWITCH SOCKET OUTLETS

        - 13 Amperes, 240 Volts, switch socket outlets shall be provided for the connection of portable electrical appliances throughout the building. They shall be switched, flat pin pattern to B. S1363: Part 2-1995, accepting 3 pin fused plugs.

        - Generally, socket outlet face plate shall be finished in white similar to the lighting switches.

        - Socket outlets shall be mounted in flush metal box. Where surface mounted socket outlets are required, they shall be similar to that of the flush pattern, mounted on suitable adapter boxes.

        - Sockets in public areas, rooms, etc. shall be with decorative face plate as per ID.  If sockets are hidden by furniture it may be non-decorative standard based on the ID drawings and approval.

        - Socket outlets provided in services plant rooms shall be metal clad type, surface or flush mounted as indicated elsewhere.

        - Weatherproof socket outlets shall be provided with push-on cap retaining ring without switch.

        - All surface mounted socket outlets shall be provided with a 13 A unbreakable plug top complete with fuse. Each twin socket shall be counted as two socket outlets.

        - Socket outlets connected to UPS shall be discriminated by graving.

        - Sockets shall be universal type within Guest rooms and wherever indicated on drawings.

      - INDUSTRIAL SOCKET OUTLETS

        - Industrial socket outlets shall be single or multi-phase, of the types and ratings as indicated on the Drawings and schedules.

        - Socket outlets shall have an enclosure of IP44 or IP67, integrated with switch or without it, as shown on the Drawings and required on site.

        - Single phase socket outlets shall be with two poles and grounding pin and three phase socket outlets shall be with three poles and grounding pin, with or without neutral pin, as shown on the Drawings and required on site.

        - The industrial socket outlets shall be designed so that the grounding pole is permanently connected to the housing. The grounding pole shall make contact before the line poles are engaged, when the plug is inserted into the socket.

        - The plug sleeve shall also make contact with the housing of socket outlet, before the line and load poles make contact.

        - The industrial socket outlets shall include cast back box, angle adapter, gaskets and a screw type gasketted watertight cap with chain fastener.

        - Each industrial socket outlet shall be provided with plug from the same manufacturer as that of the socket outlet.

      - ISOLATORS AND SWITCH FUSE UNITS

        - The isolators and switch fuse units for small power applications shall be of the double pole or three poles, single throw type, complying with the requirements of BS and other standards mentioned elsewhere in the Specifications.

        - Finishes of all isolators and switch fuse units shall be either of white plastic for flush mounted installations or rust proof metal for surface mounted installations or as directed by the Engineer on site.

        - These wiring devices shall be used for the isolation of single phase, two phase and three phase items of fixed equipment fed by an individual circuit.

        - Types of equipment fed through these wiring devices are described elsewhere in the Specification and on the Drawings.

        - All fuses in the switch fuse units shall be of HRC type, as described in Section 26 28 23.

H.     Explosion proof plugs and sockets shall have the following features as a minimum:

- Comply with IEC/EN 60309-1/-2 (CEE) and European standards EN 50014, EN 50018 and EN 50019.

- Explosion protection to CENELEC, IEC, NEC, certified for gas and dust explosion protection.

- For use in Zone 1 and Zone 2, Zone 21 and Zone 22

- Type of Protection IP 66.

- With optimal contact by means of laminated contacts individually encapsulated pins, flexibly embedded Switches.

- With large handle, can be locked in 0 and 1 position indication.

- 230V, 3 pin 16A, or 400V, 5 Pin 16A as shown on the drawings and mentioned in the BOQ.

      - SPUR OR FUSED CONNECTION UNITS

        - Spur or fused connection units shall be one complete unit combining a double pole switch, and a pilot light for confirmation that the unit is turned on.

        - The current and voltage rating of the spur or fused connection units shall be in accordance with the power requirements of the equipment to be fed.

        - All surface mounted spur units, with the exception of those to be installed in services and plant rooms, shall be mounted on metal or plastic purpose-made mounting boxes of the same material as that of the front plates.

        - In plant rooms and services rooms, spur units shall be of the surface mounted type and shall be metal clad.

      - OUTLETS FOR LOW CURRENT SYSTEMS

        - The outlets for all low current systems such as telephone, data, etc. shall conform to the requirements given in respective sections of low current systems contained elsewhere in these Specifications.

        - The cover or face plates of the outlets for all low current systems shall be of similar style and finish to that specified for the associated lighting switches and socket outlets and shall be suitable for mounting recessed or surface as required on site.

        - Sockets in public areas, rooms….etc. shall be with decorative face plate as per ID.  If sockets are hidden by furniture it may be non-decorative standard based on the ID drawings and approval.

        - Unless otherwise specified, telephone and data outlet plates shall be complete with a terminal box suitable for termination of 4 pair cable as minimum and a cable clamp to secure the outgoing telephone handset connecting cable.

        - Unless otherwise specified, TV outlet plates shall be complete with one co-axial socket outlet. Where twin outlets are required to provide both FM/Radio and TV signals, they shall be complete with duplexing network as necessary.

      - CEILING ROSE

        - Ceiling roses shall be of approved manufacture and finished as switches confirming to BS 67:1987 and BS 4568 Part 2. Ceiling roses shall be of the plug in type with 4 terminals (L, N, and Loop-In & E). Ceiling rose shall be of the funnel shaped cable entry. Heat resistant PVC insulated and sheathed flexible cable shall be provided to BS 6141:1981.

      - DISCONNECT SWITCHES

        - Disconnect Switches shall be UL listed, surface mounted, heavy duty type, sheet steel enclosed of the types, sizes and electrical characteristics suitable for the intended applications of motor, circuit or equipment disconnections as shown on the Drawings, Schedules and elsewhere in the Specifications.

        - The general duty type disconnect switches shall be rated for 240/400 Volts, 50 Hertz with 2/3 -blades, 2/3 poles, incorporating spring assisted, quick-make, quick-break type switches which are so constructed that switch blades are visible in OFF position with door open.

        - The heavy duty type disconnects or safety switches shall be fusible type, rated 500 Volts, 50 Hertz, 3-blades, 4-poles, solid neutral, incorporating spring assisted quick-make, quick break type switches which are so constructed that switch blades are visible in OFF position. These shall have positive pressure type reinforced fuse clips.

        - Equip with operating handle which shall be an integral part of enclosure base and whose position is easily recognizable, and is capable of being padlocked in OFF position.

        - Current carrying parts of all types of disconnect switches shall be constructed using high-conductivity copper, with silver-tungsten type switch contacts and stamped enclosure knockouts.

        - HRC fuses for heavy duty safety switches shall be of the classes, types and ratings needed to fulfill electrical requirements for services indicated and as recommended by the manufacturer. The fuses shall be in accordance with the requirements given in Section      26 28 23.

        - All outdoor disconnect switches shall be weatherproof, stainless steel enclosures suitable for wet and damp locations, and rust and dust-proof. These shall have appropriate heat resistant gasket to provide protection against dust and water.

      - ISOLATORS AND SWITCH FUSE UNITS

        - The isolators and switch fuse units for small power applications shall be either of white plastic or rust proof metal.

      - PUSH BUTTON STATIONS

        - All push buttons shall be made of non-hygroscopic materials, non-swelling and fitted to avoid any possibility of sticking. Non-retaining type shall generally be used except for emergency stop push buttons which shall stay down when operated and be fitted with mushroom type heads.

        - Contacts of all push buttons shall be strong and have a positive wiping action when operated.

        - All push button stations shall be provided with labels.

        - All push button stations in plant rooms, outdoor or wet locations shall be within weatherproof enclosure with appropriate heat and weather resistant gasket.

- EXECUTION

      - INSPECTION

        - Examine areas and conditions under which wiring devices are to be installed and correct any unsatisfactory conditions detrimental to proper and timely completion of the Work. Do not proceed with the work until unsatisfactory conditions have been corrected in a manner acceptable to the Engineer.

        - Coordinate the exact location and mounting heights of all wiring devices with architectural, interior design and plant / equipment layouts, location of doors, loose and fixed furniture, equipment and accessories, other services, piping, etc. Any discrepancy between electrical drawings and other disciplines/details shall be brought to the attention of Engineer.

      - INSTALLATION OF WIRING DEVICES

        - Install wiring devices where indicated, in accordance with manufacturer's written instructions, applicable requirements of Local Standards, IEE Wiring Regulations and in accordance with recognized industry practices to ensure that products serve their intended function.

        - Program installation of devices after wiring is completed and tested for satisfactory insulation resistance.

        - Install devices only in electrical boxes which are clean and free from any external building materials, debris, etc.

        - In walls or ceilings of concrete, tile or other non-combustible material, boxes and fittings install boxes and fittings so that the front edge of the box or fitting will not be set back from the finished surface more than 5 mm. In walls and ceilings constructed of wood or other combustible material, outlet boxes and fittings shall be flush with the finished surface or project there from.

        - Plaster surfaces around the back boxes of the wiring devices that are broken or incomplete, shall be repaired so that there will be no gaps or open spaces at the edge of the box or fittings.

        - In making an exposed surface extension from an existing outlet of concealed wiring, a box or an extension ring shall be mounted over the original box and electrically & mechanically secured to it.

        - All wiring devices shall be fixed independently of the system of wiring. All fixing screws or bolts shall be of steel and where the appropriate apparatus has a protective coating of zinc or is mounted outside, an electro-galvanized finish shall be used complying with relevant standards and codes of practice.

        - Install switches on the lock side of the door with 20cm distance to the centre of the first plate from the outer edge of the door frame.

        - Distance between two adjacent plates shall be 20mm.

        - Provide partitioned mounting boxes where switches from more than one final sub-circuit are installed in one box. Install switches at one location using multi-gang plates only. Install switches from different distribution boards in separate boxes.

        - Obtain drawings showing interior details and finishes, make necessary adjustment to the work so that the outlets shall be properly centered.

        - Install manufacturer supplied blanking plate of the same finish and type for each empty box/draw box.

        - All metallic cover plates shall be earthed.

        - Install outlet plates with a maximum alignment tolerance of 1.5mm between adjacent outlets.

        - Test all wiring devices in accordance with the requirements of IEE regulations. Under no circumstances are the devices to be connected to main power until the tests are completed and approved by the Engineer.

      - FIELD QUALITY CONTROL

        - Check operation of all switches and wiring devices with power supply connected.

        - Check polarity of all the outlets and receptacles with polarity tester.

- END OF SECTION