- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Electrical Raceways, accessories and Boxes / Fittings including, but not limited to, the following:

            - PVC Conduits.

            - Rigid Steel Conduits.

            - Flexible Conduits.

            - Interior outlet boxes.

            - Weatherproof outlet boxes.

            - Junction/pull boxes and cabinets.

            - Floor boxes

            - Conduit bodies.

            - Fittings.

      - REFERENCES

        - The IEE Wiring Regulations, 17th Edition with all current additions and amendments.

        - BS 4568   Rigid Steel Conduits, Zinc Coated.

        - BS 6099-2.2 / IEC 614-2-2    U.P.V.C. Rigid Conduits.

        - Local Codes, Standards and Regulations.

      - SUBMITTALS

        - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

        - Product Data: Submit for the following:

          - Flexible metal conduit.

          - Liquid tight flexible metal conduit.

          - Nonmetallic conduit.

          - Flexible nonmetallic conduit.

          - Nonmetallic tubing.

          - Raceway fittings.

          - Conduit bodies.

          - Surface raceway.

          - Wire way.

          - Pull and junction boxes.

          - Handholds.

        - Method Statement and Manufacturer's Installation Instructions: Submit application conditions and limitations of use stipulated by Product testing agency specified under Regulatory Requirements. Include instructions for storage, handling, protection, examination, preparation, and installation of Product.

        - Provide samples of all proposed devices, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

      - CLOSEOUT SUBMITTALS

        - Provide samples of all proposed raceways, boxes, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Provide method statement for installation, testing and commissioning of raceways and boxes.

        - Project Record Documents:

          - Record actual routing of conduits.

          - Record actual locations and mounting heights of outlet, pull, and junction boxes.

      - COORDINATION

        - Coordinate installation of outlet boxes for equipment connected under Section 26 05 03.

        - Coordinate mounting heights, orientation and locations of outlets mounted above counters, benches, and backsplashes.

      - QUALIFICATIONS

        - Manufacturers: Firms regularly engaged in manufacture of raceways of types and ratings required, whose products have been in satisfactory use in similar service for not less than 10 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - QUALITY ASSURANCE

        - Electrical Raceways shall generally be manufacturer’s standard construction and materials.

      - DELIVERY, STORAGE AND HANDLING

        - Product Requirements for storage and handling.

        - Protect conduit from corrosion and entrance of debris by storing above grade. Provide appropriate covering.

        - Protect PVC conduit from sunlight.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - PVC CONDUITS

        - All PVC conduits and fittings shall be UPVC heavy gauge, rigid, direct buried or encased buried type as applicable, complying with BS 6099-2.2 / IEC 614-2-2 heavy gauge in all respects, and may be used where ambient temperatures do not exceed 75 oC.

        - All PVC conduits and accessories shall be obtained from the same manufacturer.

        - No conduit shall be less than 20 mm diameter.

        - Fittings and accessories for PVC conduits shall include, but not be limited to, the adapters, junction/pull boxes, bushings, couplings, elbows, nipples, plugs, seals, etc.

        - Conduit boxes shall be of the circular pattern with appropriate spout entries and 50.8 mm accessory fixing centres.

        - All connections and terminations of the PVC conduits and fittings shall be by means of the manufacturer's standard adaptor.

        - All boxes shall have brass thread inserts for the fixing of accessories or covers.

        - All tees shall be made using conduit tee boxes. Tangential entry boxes shall be used where appropriate. Multiple conduits may necessitate the use of large uPVC adaptable boxes for junctions.

        - All saddles shall be of the spacer bar type and from the same manufacturer as that of the conduit which they are being used to secure.

        - All wall mounted accessory boxes shall have one adjustable fixing lug to facilitate final leveling of accessories.

      - RIGID STEEL CONDUITS (RSC)

        - All Rigid Steel Conduits (RSC) and accessories shall be heavy gauge welded steel complying with BS 4568, not less than 20 mm diameter.

        - RSC and fittings shall be hot dipped galvanized, complying with BS 4568, and providing heavy protection both inside and outside. The steel shall be galvanized after cutting and threading.

        - All conduits and fittings shall be threaded, free from rust or other defects and shall have same hot dipped galvanized finish throughout the installation.

        - Fittings and accessories for RSC shall include, but not be limited to, adapters, junction/pull boxes, bushings, connectors, couplings, elbows, expansion joints, gaskets, hubs, locknuts, nipples, plugs, seals, breathers, etc.

        - Fittings and accessories for RSC shall be of malleable iron or a mixture of grey iron and cast steel.

        - All bushes shall be hexagonal headed, heavy duty, long threaded brass bushes complete with serrated tempered shake proof washers. All bends shall be cold set. All tees shall be made using circular tee conduit boxes.

        - All saddles for surface mounted installation of RSC shall be of the spacer bar type and of the same finish as that of the conduit which they are being used to secure.

        - A tapped earth connection facility shall be provided in every box.

        - All accessory boxes shall have one adjustable fixing lug to facilitate final levelling of accessory.

        - PVC coated RSC and fittings shall be used for cables extending to outside of building and where above grade extensions of PVC Conduits required a transition from PVC to RSC.

      - FLEXIBLE CONDUITS

        - Flexible conduits shall be liquid-tight, constructed from galvanized steel core and continuous liquid-tight PVC jacket in accordance with BS 731 Part 1, not less than 20 mm diameter.

        - Flexible conduit shall only to be used for final connection to items of fixed equipment subject to vibration or movement.

        - All flexible conduits shall have a liquid-tight PVC jacket capable of withstanding 90 oC cable operating temperatures.

        - All fittings and accessories for liquid-tight flexible steel conduits shall be nylon jacketed.

        - Nylon jacketed brass adaptors shall be provided for connection at either end of the flexible conduit and should be of the compression type.

      - CABLE TRAYS

        - All cable trays shall be of heavy duty perforated type with return flange.

        - All cable trays shall be manufactured from hot-dip zinc coated galvanized steel, with a standard heavy duty galvanizing coating of 350 g/m2 and Z2 bending grade.

        - All accessories and fittings such as bends, tees, elbows, cross units and angles shall be of the same specification as that of the cable tray finish and shall be standard products from the same manufacturer as the cable tray. Site fabrication shall not be permitted.

        - Cable trays and accessories shall be of a thickness of not less than:

          - 1.5 mm up to 305 mm width.

          - 2 mm above 305 mm width.

        - All fixing brackets, nuts and bolts shall be finished by hot dip galvanizing.

        - Tinned copper earth continuity straps shall be provided at every joint of the cable tray.

        - Where cable tray crosses building expansion joints, the tray shall be installed suitably to provide expansion / contraction with the building expansion.

        - Where cable tray carries 11 kV cable, a tray lid shall be installed.

        - In outdoor locations and areas subject to corrosive atmospheres, all cable trays shall be painted with chlorinated rubber paint or PVC/Epoxy coating, as approved by the Engineer.

      - CABLE LADDERS

        - All cable ladders shall be heavy duty gauge (>2 mm), manufactured from hot-dip galvanized steel with a standard heavy duty galvanizing coating of 350 g/m2 and Z2 bending grade.

        - All accessories and fittings such as couplers, bends, tees, elbows, etc. shall be by the same manufacturer as the ladder.

        - Ladder system supports shall be determined in accordance with the manufacturer's structural information to ensure that undue stress or bending shall not occur.

        - Tinned copper earth straps shall be provided at every joint of cable ladders.

        - In outdoor locations and areas subject to corrosive atmosphere, the ladders shall be painted with chlorinated rubber paint or PVC/Epoxy coating, as approved by the Engineer.

      - INTERIOR OUTLET BOXES

        - All interior outlet boxes shall be constructed in compliance with BS 4662 type UA1.

        - Outlet boxes shall be with 1.1mm thickness and 7x7 cm or 7x14 cm size and 3.5cm depth with adjustable lug.

        - Provide galvanized flat, rolled sheet steel interior outlets and switches wiring boxes of types, shapes, sizes and depths to suit each respective location and installation.  Construct threaded screw holes with corrosion-resistant screws for securing box covers and wiring devices.

        - Brass earthing terminal with screw shall be provided inside the box for grounding connection of all metallic outlet boxes with appropriate earth mark.

        - Accessories for interior outlet boxes such as mounted brackets, wallboard hangers, extension rings, fixture studs, grounding connection, cable clamps, metal straps for supporting outlet boxes, etc. shall be compatible with outlet boxes being used and fulfilling requirements of individual wiring situations.

        - Exposed or surface mounted boxes, when used with rigid steel conduits, shall have threaded hubs. These boxes shall be cast from malleable iron, hot-dip galvanized.

      - WEATHERPROOF OUTLET BOXES

        - All weatherproof outlet boxes shall comply with BS.

        - Provide corrosion-resistant cast metal weatherproof outlet wiring boxes of types, shapes, sizes and depths to suit each location and installation as shown on the Drawings.

        - Weatherproof outlet boxes shall be provided with threaded conduit ends, terminal with screw for ground connection, cast metal face plates with spring-hinged waterproof caps, suitable configures for each application, including face plate gaskets and corrosion resistant fasteners.

        - All weatherproof outlet boxes shall be provided with corrosion free epoxy powder coat, to provide corrosion resistance with appropriate gasket.

        - For outdoor applications and areas with corrosive atmosphere, boxes for use with PVC coated steel conduits shall be galvanized cast boxes with a PVC factory applied coating of 40 mm minimum thickness.  Boxes shall have hubs with extruded sleeves extending the hubs.

      - JUNCTION/PULL BOXES AND CABINETS

        - All junction and pull boxes shall be constructed in compliance with BS.

        - Provide galvanized, code gauge sheet steel junction and pull boxes with screws on cover, of types, shapes, sizes and depths to suit each respective location and installation.

        - Junction/pull boxes and cabinets shall be provided with welded seams and appropriate cast covers, equipped with stainless steel nuts, bolts, screws, washers and terminal with screw for ground connection.

        - Junction/pull boxes and cabinets/enclosures shall be provided with hinged covers, where required.

        - Cabinets shall be provided with a reinforced steel back plate for mounting interior components, rigidity and accurate alignment.

      - FLOOR BOXES

        - All floor outlet boxes shall be metallic and constructed in compliance with BS.

        - Provide corrosion resistant, galvanized, sheet steel floor outlet boxes of the types, shapes, sizes and depths to suit each respective location and installation.

        - The depth of floor outlet boxes shall be sufficient enough to accommodate conduit entries from sides and all kind of wiring devices with plugs from the top.

        - The floor outlet boxes shall be waterproof when fully closed.  Appropriate rubber protection shall be available for cable outlets from the floor base.

        - The cover of the floor outlet boxes shall be able to be closed completely after installation of plugs and connecting devices inside the box.  The cover shall be suitable for flush floor installation with provision of fixing carpet, vinyl sheet, etc. above the cover to match with the finish of the floor.

        - Floor boxes shall have a panel opening and overall module depth shall be suitable for the required compartments. The box must be provided with total Device Wiring Chamber.

        - The box lid shall be a hinged style and constructed of polycarbonate material, available in standard colors of black, brown and gray. The lid shall provide a minimum of three removable cable guards for egress of power and communication workstation cables. The cable guards shall hold workstation cables in place with the lid either in the open or closed position.

        - The trim flange shall be constructed of polycarbonate material. The hinged lid and trim flange shall be available for either carpet or tile floor applications.

        - The wiring chamber shall provide an upper and a lower compartment. The top compartment shall be divided into four separate compartments to accommodate a combination of both power and communication wiring as indicated on drawings. These compartments shall be separated by use of integral; die cast aluminum built in dividers. The bottom compartment shall be available for either all power or all communication wiring.

        - The box shall be secured to the raised floor by the use of two locking tabs. The locking tabs shall be integral to the box and adjusted by use of their locking screws.

      - CONDUIT BODIES

        - All conduit bodies such as capped elbows and service entrance elbows shall be constructed in compliance with BS.

        - Conduit bodies and covers shall be constructed from the same material and shall have the same finish or protective coating as that of associated conduits.

        - Provide galvanized conduit bodies of types, shapes and sizes to suit respective locations and installation, with thread corrosion-resistant screws for fixing.

        - The conduit bodies shall be appropriately threaded for the conduits and equipped with corrosion resistant screws for fixing the inspection cover.

        - Weatherproof conduit bodies and covers shall be provided with corrosion free epoxy powder coat, to provide resistance again corrosion.  Covers shall be gasketted.

      - FITTINGS

        - Provide corrosion-resistant punched-steel box knockout closures, conduit locknuts and malleable iron conduit bushings, offset connectors, covers of types and sizes to suit respective uses and installation.

        - Covers of junction/pull boxes, cabinets/enclosures, etc. shall be of the same thickness and material as that of the box and shall be reinforced where required due to large size.  Screws for covers shall be stainless steel or high quality brass.

- EXECUTION

      - RACEWAYS

        - INSPECTION

          - All Electrical Raceways including conduits and fittings shall be free from objectionable lines, striations, bubbles, welds, and other manufacturing defects that would impair the service of the raceways. The bore of the conduits shall be circular in cross-section with smooth interior surfaces free from rough and flaky areas. The electrical raceways and fittings shall be free from all substances that injuriously effect any wire or cable covering.

          - All the Electrical Raceways including conduit runs are shown diagrammatically on the Drawings to outline the general routing only. Any interference with pipes, HVAC ducts, structural members or other equipment shall be inspected and coordinated well before commencement of the installation of raceways. Deviations shall be made in accordance with the approval of the Engineer, at no extra cost to the Contract.

        - PVC CONDUITs INSTALLATION

          - PVC conduits shall be used only where cast into slabs, built or chased into walls etc. Where conduits are surface run in ceiling voids, shaft spaces, plant rooms etc. galvanised RSC shall be used. Adaptation between PVC and metal conduits shall be through metal boxes.

          - PVC conduits shall not be installed in locations exposed to direct sun light.

          - Where conduit boxes are not to be fitted with accessories, they shall be fitted with cover plates which shall be overlapping where flush boxes are used.

          - PVC conduits shall be jointed and terminated utilizing the following appropriate components as supplied by the conduit manufacturer:

            - Purpose made adaptors and accessories.

            - Permanent adhesive - Solvent cement to produce a rigid watertight joint when used with standard couplers and accessories.

            - Flexible adhesive - A non-hardening adhesive to be used where expansion facilities are required in long conduit runs, in conjunction with expansion coupler. Not to be used at building movement joints.

          - PVC conduits up to 25 mm diameter may be bent cold with the use of the appropriate bending spring obtained from the conduit manufacturer. For larger size conduits, it is necessary to use heat or appropriate manufacturer's standard ready-made bends.

          - Adequate allowance shall be made for linear expansion and contraction of the conduits under normal working temperature variations, as follows:

            - Conduit shall be free to slide within saddles.

            - Allowance for expansion in cast in-situ installation is normally only required to effect structural movement at building expansion joints.

            - Expansion couplers shall be used on all straight runs of conduit exceeding 6 m in length.

          - Conduit shall be supported at intervals of 1.5 m in isolated positions or 1 m in accessible situations. Where working temperatures are high, this spacing shall be reduced accordingly.

          - Multiple conduits may necessitate the use of large PVC adaptable boxes for junctions, which shall be readily accessible at all times.

          - Care shall be taken in the support of totally enclosed lighting fittings. Where excessive temperatures are likely to occur, special heat resistant boxes shall be used, i.e. of a pattern specifically designed to improve weight loading characteristics at high temperatures.

          - Spacing (fill) factors shall be applied to all conduit in accordance with 522-08 of the IEE Wiring Regulations, 18th Edition (BS7671).

          - Do not install PVC conduits closer than 75 mm to pipes of other services.

          - "Draw-in" boxes shall be installed in all conduit runs exceeding 3 m in length at a maximum 12 m spacing and shall be readily accessible at all times.

          - Inspection elbows, bends or tees shall not be permitted for flush installation.

          - Use extension rings where boxes are found to be not flush with the finished surface. Care shall be taken to prevent water, dirt, dust or debris from entering the conduit system.

          - All bends shall be made so that the PVC conduits shall not be damaged, and the internal diameter of the conduits shall not be effectively reduced.

          - Not more than four 90 degree bends nor a total of 360 degree bends shall be made in one conduit run between outlets, fittings or outlet bodies including any bends located immediately at the start or end.

          - Install concealed conduits such that only two crossings at a given point are allowed within the slab to prevent any damage or cracking of slab.

          - No conduit shall be allowed to run in the floor screed of toilets, kitchen, bathroom or any other wet area.

          - Where cables pass through ducts or sleeves entering buildings, seal the ends of the ducts or sleeves using a special caulking compound of a putty-like consistency. It shall be workable with the hands at temperatures as low as 1.7 oC, and shall not slump upto a temperature of 149 oC or less. It shall not be hardened materially when exposed to air.

        - METAL CONDUIT INSTALLATION

          - Metal conduits either Rigid Steel Conduits (RSC) shall be installed in exposed locations as required. RCS shall be installed exposed on surface at all such locations where conduits are liable to be damaged mechanically.

          - Threads for RSCs shall be of sufficient length to allow conduits to butt together within couplers. A minimum engagement of five (5) full threads shall be made at all fittings and accessories.

          - Remove oil and grease from all threads of RSCs.

          - Support all metal conduits at intervals of 1.5 m in isolated positions or 1 m in accessible situations.

          - Do not install metal conduit closer than 75 mm to pipes of other services.

          - All conduit boxes not to be fitted with accessories shall have metal cover plates which shall be overlapping where flush boxes are used.

          - 'Draw in' boxes shall be provided in conduit runs exceeding 3 m in length. 'Draw in' boxes shall be at a maximum 12 m spacing and readily accessible at all times. Adaptable junction boxes shall also be accessible at all times for inspection and maintenance.

          - Exercise care shall be taken to prevent water, dirt and debris from entering the conduit system.

          - Use extension rings where boxes are found not to be flush with the finished surface.

          - Protect conduits and conduit accessories from rust and mechanical damage. Exposed conduit threads and damaged or rusty portion of metal conduits shall be painted, using an oxide undercoat and aluminum paint, after being cleaned to bare metal.

          - Conduits installed in areas subject to corrosive atmospheres shall be painted with chlorinated rubber paint after the installation is complete.

          - Under no circumstances, shall any metal conduit be used as a circuit protective conductor (CPC). Every final sub-circuit shall incorporate its own separate Cu/PVC CPC.

          - Spacing (fill) factors shall be applied to all conduits in accordance with 522-08 of the IEE Wiring Regulations, 17th Edition (BS7671).

          - Field bends shall be made with a hand bender for 1-1/2” (38mm) and smaller diameter metal conduits only. Larger size conduits shall be bent with a machine bender or be factory supplied. Heating of metal conduits to facilitate bending is not permitted.

          - All bends shall be made so that metal conduits shall not be damaged, and the internal diameter of the conduit shall not be effectively reduced. The inner edge radius of all field bends shall not be less than the minimum allowable radius as BS.

          - Not more than four 90 degree bends nor a total of 360 degree bends shall be made in one conduit run between outlets, fittings or outlet bodies including any bends located immediately at the start or end.

          - Conduits and elbow used for cables extending to outside of building shall be PVC coated rigid steel extending one meter from building foundation. A concrete encased PVC adapter shall be used in case cable extending will run in PVC ducts. Bells shall be provided on PVC horizontal stub outs.

          - PVC conduits shall not be extended above grade. Where extensions of PVC conduits above grade are required, a PVC coated rigid steel transition bend having PVC/steel coupling on one end and threaded male or female adaptor on the other end. The PVC coated rigid steel transition bend or conduit shall extend minimum 150 mm above grade. A concrete envelope 100 mm high shall be formed around such risers to minimize corrosion at point of emergence. The top of the envelope shall be sloped for drainage.

          - Verify exact stub up location and termination requirement for items and equipment being served, for all necessary power and control wiring.

          - Where cables pass through ducts or sleeves entering buildings, seal the ends of the ducts or sleeves using a special caulking compound of a putty-like consistency. It shall be workable with the hands at temperatures as low as 1.7 oC, and shall not slump up to a temperature of 149 oC or less. It shall not be hardened materially when exposed to air.

          - Where conduits turn out of, or penetrate, a slab, they shall be not less than 65 mm on centers.

          - Location and sizing of conduit sleeves passing through floors and walls that are not shown on the Drawings shall be the responsibility of the Contractor. All sleeves shall be rigid galvanized steel unless indicated otherwise, extended 150 mm above floor and capped when not in use. Space between conduits and sleeves shall be filled with ductseal to a minimum of 50 mm deep at top and bottom of conduit sleeve.

          - All metal conduits entering any gasketed boxes or gasketed equipment enclosure shall be provided and terminated with gasketed hubs with bonding screws. Whereas the metal conduits entering non-gasketed sheet-metal boxes or enclosures shall be provided and terminated with general purpose hubs.

          - Provide supports to alleviate stress on cables where they enter a conduit or other enclosure from the tray.

        - FLEXIBLE CONDUITs INSTALLATION

          - All flexible conduits and fittings used shall be liquid-tight.

          - Flexible conduits shall only be used in short lengths, of less than 1000 mm, in cases where a final connection is required to be made to a fixed item of equipment which is subject to vibration or thermal expansion.

          - Flexible conduits shall be 1.25 x L in length, L being the direct distance between connection unit and fixed appliance, up to maximum length of 1 m.

          - Purpose made glands shall be used on the ends of all lengths of flexible conduits.

          - A separate Cu/PVC circuit protective conductor shall be included in all lengths of flexible conduits.

          - Flexible conduits shall be installed so as not to incur undue mechanical strain, damage or excessive temperatures.

        - CABLE TRAYS/LADDERS INSTALLATION

          - Where practical, cable trays/ladders shall be run horizontally and flat or vertically and shall be supported at distances not exceeding 1.5 m to the building structure using mild steel brackets. These brackets shall be secured to the building structure using expanded bolts and washers or built into the building structures during construction.

          - Where cable tray/ladder is suspended, 2 drop rods shall be used at each suspension point to an angle iron or channel support to which the cable ladder is bolted. The spacing of suspension points shall be determined in accordance with the manufacturer's structural information such that undue stress of defection does not occur.

          - Where cable tray/ladder is cut, the open ends shall be painted using an oxide undercoat and an aluminum top coat. Where the finish is PVC, a top coat of liquid PVC solution shall be applied after the completion of the cable ladder installation.

          - Cable trays/ladders run parallel with walls shall not be mounted closer than 75 mm to the wall.

          - All cables shall be secured to the cable tray with clamps at distances in accordance with 522-08 of the IEE Wiring Regulations, 17th Edition (BS7671).

          - Do not run bare copper or aluminum cables run on cable tray/ladder.

          - Ensure earth continuity by means of tinned copper earth straps bolted across each cable tray/ladder joint. Flexible braided straps shall be used for expansion joints.

      - BOXES

        - PREPARATION

          - Determine exact locations of outlets on site after co-ordination with layouts for architectural, furniture and other equipment.

          - The locations of junction/pull boxes and other fittings and accessories are generally not shown on the Drawings, but Contractor shall provide these in compliance with applicable requirements of IEE Wiring Regulations, ease of maintenance, manufacturer’s written instructions and recognized industry practices.

        - INSTALLATION

          - Install all electrical boxes and fittings in accordance with IEE Wiring Regulations.

          - Coordinate installation of electrical boxes and fitting with wire/cable and raceway installation work.

          - Provide knockout closures in all types of electrical boxes to cap unused knockout holes where blanks have been removed.

          - Install all types of boxes and conduit bodies at accessible locations to ensure easy installation and maintenance of electrical wiring.

          - Avoid using round boxes where conduit must enter box through side of box, which would result in difficult and insecure connections when fastened with locknut or bushing on rounded surface.

          - Fasten boxes rigidly to substrate or structural surfaces to which attached, or solidly embed electrical boxes in concrete or masonry.

          - Provide electrical and earth connections for all types of installed electrical boxes.

          - Fastenings for all types of exposed/surface mounted electrical boxes shall not penetrate more than 30 mm into reinforced concrete beams or more than 20 mm into reinforced concrete joists and shall not contact main reinforcing steel.

          - Boxes and supports shall be fastened with toggle bolts on hollow masonry units, and with machine screws or welded studs on steel work.

          - In open overhead spaces, cast metal boxes threaded to raceways need not be separately supported except where used for fixture support.  Support cast metal boxes having threadless connectors and sheet metal boxes directly from the building structure or with bar hangers.

          - Where conduit supported outlet boxes are installed and conduit suspended from the structure with hangers, attach hangers to raceways on opposite sides of the box and shall be supported with an approved type fastener not more than 1 m measured each side from the box.

          - Boxes installed outdoor on concrete or masonry walls, for vaportight fixtures, shall be weatherproof type.

          - Provide weatherproof outlets for interior and exterior locations exposed to weather or moisture or where shown on the Drawings.

          - Interior or weatherproof outlet boxes shall be provided for each light fixture, receptacle, equipment connection and other conduit termination points.

          - In suspended ceilings where outlet boxes support fixtures in which the ceiling suspension system does not have sufficient strength to prevent visible deflection of the ceiling surfaces, the boxes shall be supported by structural members, secured to building structure.

          - Outlet box covers shall not be used to support fixtures.

          - Requirement of pull boxes shall be determined based on maximum allowable conduit runs, as described in Section 26 27 26.

          - Where pull boxes (existing and new), are connected to conduits running underground in the site, they shall be provided with suitable provisions for drain.

      - INTERFACE WITH OTHER PRODUCTS

          - Install conduit to preserve fire resistance rating of partitions and other elements, using materials and methods in accordance with Section 07 84 00.

          - Route conduit through roof openings for piping and ductwork or through suitable roof jack with pitch pocket. Coordinate location with roofing installation.

          - Locate outlet boxes to allow luminaries positioned as indicated on Drawings reflected ceiling plan.

          - Align adjacent wall mounted outlet boxes for switches, thermostats, and similar devices

      - ADJUSTING

          - Execution Requirements: Testing, adjusting, and balancing.

          - Adjust flush-mounting outlets to make front flush with finished wall material.

          - Install knockout closures in unused openings in boxes.

      - CLEANING

          - Execution Requirements: Final cleaning.

          - Clean interior of boxes to remove dust, debris, and other material.

          - Clean exposed surfaces and restore finish.

- END OF SECTION