- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - LV Protective Devices installed in LV switchgears, power distribution boards, panel boards, motor control centers, control panels including, but not limited to, the following:

            - Air circuit breakers.

            - Molded case circuit breakers.

            - Miniature circuit breakers.

            - Residual current circuit breakers.

      - REFERENCES

        - IEC 60947-1: LV Switchgear & Control Gear – General rules

        - IEC 60947-2: Circuit breakers

        - IEC 60898: Circuit breakers for over current protection (MCB)

        - IEC 601008: Residual Current Operated Circuit breakers without integral over current protection (RCCB)

        - IEC 601009: Residual Current Operated Circuit breakers with integral over current protection (RCBO)

        - IEC 60755: General requirements for residual current operated devices.

        - I EC 60947-3: Switches, Disconnectors, Switch- disconnectors & Fuse combination unit

        - IEC 60947-4 (1 to 3 parts : Contactors and motor starters

        - IEC 60947- 5 (1 to 9 parts): Control circuit devices and Switching elements

        - IEC 60947- 6 (1 to 2 parts : Multiple function equipment –Transfer Switching, Control & protective switching devices

        - IEC 60947- 7 (1 to 3parts) Ancillary Equipment’s – terminal Blocks

        - IEC 60051 (1 to 9 parts)	Direct Acting Indicating Analog Electrical Measuring Instrument & their accessories

        - IEC 60127 (1 to 6 Parts)	: Miniature Fuses

        - IEC 60127: Specification for Cartridge Fuses for A.C circuit in Domestic and similar Premises.

        - IEC 60269 (Part 1 to 4), BS 88: Specification for Cartridge Fuses for voltage up.

        - IEC I57 Air Circuit Breakers (ACB)

        - BS EN 60947   Molded Case Circuit Breakers.

        - Local Codes and Regulations.

      - SUBMITTALS

        - Submit for complete and detailed manufacturer's catalogues and data relating which shall include, but not limited to, the following:

          - Name of the manufacturer.

          - Country of origin.

          - Name and address of agents stating whether any manufacturing or fabrication is carried out in Jordan.

          - Method of obtaining spare parts for maintenance and list of spare parts sufficient for a 2 years’ period.

          - Technical performance of the equipment selected.

          - Dimensional details needed for installation and maintenance.

          - Delivery time from the date of orders.

          - Copies of test reports or certificates.

          - Control schematics and wiring diagrams.

        - Provide samples of all proposed devices, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Submit factory test reports verifying that all the LV protective devices have successfully passed all routine and type tests.

        - Submit Method Statement for installation, testing, commissioning and operation of proposed devices.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations and continuous current ratings of enclosed circuit breakers.

      - QUALIFICATIONS

        - Manufacturer: Company specialized in manufacturing the products specified in this section with minimum ten years documented experience

        - All components for the project shall be offered from one manufacturer to ensure proper protection co-ordinations and easy substitution.

      - QUALITY ASSURANCE

        - All LV protective devices to be UL listed and conform to the requirements of BS, IEC and Local Standards Organization.

      - SPARE PARTS

        - Supply as maintenance stock, additional LV protective devices of all types and ratings, amounting to one unit for every 10 installed units, but not less than two units of each type and rating.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - GENERAL

        - All materials specified herein shall be of high quality and of proven suitability for the functions they will perform and the conditions they will meet in services.

        - For remote monitoring/controls, comply with the requirements as given in Section 23 20 00.

      - AIR CIRCUIT BREAKERS

        - The Air Circuit Breakers (ACB) shall be fully withdrawable type designed to comply with BS.4752 and/or IEC I57, and have a short circuit level for 65 KA at 1 Sec.

        - The air circuit breakers shall be with draw able type with current monitor and solid state sensor for phase and earth sensing protection. The static sensor shall have adjustable settings for each of the following tripping characteristics:

          - Long - delay pick up point.

          - Long - delay tripping time.

          - Short - delay pick up point (Instantaneous protection).

          - Earth point pick up.

          - Earth tripping time.

        - Extra facilities are required such as shunt trips, under voltage release, auxiliary switches, self-indications monitor, load monitoring, measurement of phase currents, maximum current and fault currents.

        - The Air Circuit Breaker shall be designed as a completely self-contained cassette unit which can be mounted in an LV panel compartment without additional screening. Safe access for routine maintenance shall be provided by lockable automatic safety shutters within the cassette.

        - A motorized operating mechanism shall be provided of the trip free type to enable the facility of slow closing to allow checking of operation and adjustment.

        - The A.C.B's must have the following 3 distinct positions (draw out version):

          - Fully inserted position.

          - Test position.

          - Isolated position.

        - A front operated racking mechanism shall withdraw the ACB. The racking mechanism is still engaged in the isolated position, which allows testing of control circuits. Further racking releases the ACB and the breaker can be withdrawn for inspection. A flag indicator will show the breaker position.

        - ACB shall come with a transparent hinged and secured cover (IP54).

        - Mechanical Interlocks shall prevent the following:

          - The ACB being isolated unless it is in the off position.

          - The ACB being racked into the service position unless it is in the off position.

          - The ACB being accidentally pulled off the guide rail.

          - The ACB being slow closed in the service position.

          - Access to the racking mechanism unless the ACB is in the off position.

        - Each Air Circuit Breaker shall incorporate a microprocessor based sensing protection/information unit. The unit shall be adjustable for long time delay, short time delay, instantaneous trip and earth fault.

        - The microprocessor unit shall have a high resolution screen display, which shall be capable of showing the following functions of the unit:

          - Measurements of V, A, W, VAR, VA, Wh, VARh, VAh Hz, Vpeak, Apeak, power factor and maximeters and minimeters.

          - Long time protection, minimum and maximum voltage and frequency, voltage and current imbalance, phase sequence, reverse power.

          - Load shedding and reconnection depending on power or current

          - Measurements of interrupted currents, differentiated fault indications, maintenance indications, event histories and time-stamping etc.

          - Power quality: fundamentals, distortion, amplitude & phase of harmonics up to the 6th order.

          - Waveform capture after fault, alarm or on request

          - Enhanced alarm programming: thresholds and actions

      - MOULDED CASE CIRCUIT BREAKERS

        - Molded case circuit breakers (MCCB’s) shall comply with BS EN 60947-1 & 2:1992. They shall be of the quick-make, quick-break, trip-free, thermal magnetic adjustable releases for rating lower than 160A, and with solid state trip units for rating 160A an above. Breakers shall be complete with De-ion arc grids, alloys contacts and inter-pole contacts. All units shall incorporate a visual indication of open or closed contacts.

        - Extra facilities may be required, such as shunt trips, under-voltage release, auxiliary switches, remote indications or tripping, residual current protection or special calibrations. Such extra facilities shall be specified elsewhere in this Specification or as shown on the Drawings.

        - The short circuit interrupting capacity of all MCCB’s in any panel boards; SMDB, MCC, power distribution board/switchboard, control panel, etc. shall not be less than the max. Short circuit rating of the main bus bars, as shown on the Drawings and Schedules.

      - MINIATURE CIRCUIT BREAKERS (MCB’s)

        - Miniature circuit breakers (MCB’s) shall be plastic molded units incorporating thermal magnetic protection against overloads and short circuits comply with IEC/BS Standards. The tripping mechanism shall be designed to provide delays operation on overload and instantaneous operation under fault condition. Breakers shall have positive ON/OFF indication, be "trip free" and shall trip to the full off position under overload and/or short circuits. Triple pole units shall be used for three phase circuits. All multiple breakers shall have an integral common trip bar as standard.

        - MCBs shall be able to withstand 10KA short circuit rupturing capacity.

        - Where the fault level of the system is such that the use of MCB’s is not acceptable, then molded case circuit breakers (MCCB’s) as specified elsewhere shall be utilized.

      - EARTH FAULT PROTECTIVE DEVICES

        - Earth Fault Relays

          - Used in conjunction with shunt trip of MCB or MCCB.

          - Relay shall comply with IEC 60255 & IEC 60755 and will be site adjustable for current sensitivity and time delay.

          - Shall be Solid state type, self-protected from high magnitude earth faults and protected against dirt, vibration and moisture.

          - Adjustable sensibility from 0.03A to 30A. The relay shall have time delay from instantaneous to 5 seconds (minimum 1 second).

          - Relay shall be equipped with one changeover output contact. The continuity of the measurement circuit shall be monitored to ensure that the toroid circuit is not open.

          - Shall be compact in size and suitable for mounting on symmetrical rail horizontally or vertically. Shall be protected against nuisance tripping caused switching surges or by lighting surges.

      - HRC FUSES

        - Fuses shall be HRC Class Q1 to BS 88, Part 2 or IEC-60269 Part 1 and 2.

        - HRC fuses shall be ASTA certified.

      - CONNECTIONS

        - Connection to starter sections above 100A shall be with bus bars. PVC insulated cables may be used for lesser currents.

      - METERING

        - Meters

          - Provide digital totalazing type, polyphase voltage, current, frequency, power factor, kVA, kW and accumulating total of MWHR and kW.

          - Provide digital meters on all main incoming breakers.

          - Provide line drivers for remote sensing on the BMS. Coordinate with BMS supplies.

          - Moving iron type meters with jewel bearing, spring loaded and silicone oil damper. Accuracy Class 1.5 to DIN 43780.

          - Case of glass filled polycarbonate with dimensions of 72 x 72mm for branch circuits and wall mounted panels and 96mm x 96mm for free standing panels. Non reflective glass window.

          - Overload limit in accordance with DIN 43780.

          - Life time test: 150,000 full scale deflections with 1 sec ON after steady state and 4 sec. OFF.

          - Rated insulation voltage: 1 000V.

          - Measuring range:

            - Voltmeter - 0 - 600 V

            - Ammeter - within +25% of the maximum current expected the circuit.

          - Ammeter connected to feeder line of switchboards shall have an additional maximum demand indicator.

          - Provide ammeter and voltmeter with selector switch for each motor and heater loads although not shown on the drawings.

          - Provide with current transformers where required.

      - EARTH LEAKAGE RELAYS WITH SEPARATE SENSOR

        - Relays complying with IEC 60755 and of solid state type protected from nuisance tripping caused by surges. Provide with sensitivity adjustment in steps from 0.03A and step time adjustment from instantaneous to 1 second. Toroidal transformers are to be of suitable diameter to fit on the cables.

        - Provide earth leakage relays for all circuits connected to shunt trip of breakers or with audio visual alarm as shown on drawings. The common alarm horn shall be flush mounted on panel face with a separate lamp for each relay. Provide with wiring terminated on suitable terminal blocks for remote indication of alarms.

      - MOTOR PROTECTION CIRCUIT BREAKER

        - Provide short circuit protection for the motor circuits with molded case circuit breakers co-ordinated with the thermal relay and contactors to provide type 2 coordination as defined by IEC 60947-4.1. Adjustable magnetic protection shall range from 6 to 12 times the nominal current rating. Breaking capacity to be as shown on drawings. Provide with shunt trip and 3 auxiliary contacts for BAS.

      - CONTACTORS

        - Provide contactors conforming to IEC 60947-4 selected to utilization category AC-1 for heater loads and category AC-3 for motor loads. All ratings shall be selected for an ambient temperature of 45 °C with normal operating current of motor less than 0.1 of the rated making current of the contactor.

      - THERMAL OVERLOAD RELAYS

        - 660 V bimetallic relays rated according to IEC 60292-1 with tripping class 10 according to IEC 60947-4. Provide with terminal blocks facility to lock in "stop" position, and with test button to enable checking of control wiring and to simulate relay tripping. The trip setting shall be lockable after setting.

- EXECUTION

      - INSTALLATION

        - Install protective devices as indicated, in accordance with manufacturer's written instructions and with recognized industry practices to ensure compliance with BS, IEC and Local Standards and Regulations.

        - Coordinate with other work, including electrical wiring work as necessary to interface installation of protective devices with other work.

        - Fasten circuit breakers without mechanical stresses, twisting or misalignment being exerted by clamps, supports or cable.

        - Set field-adjustable circuit breakers for trip settings as indicated, subsequent to installation of devices.

        - Install fuses, if any, in fused circuit breakers.

        - Inspect circuit-breaker operating mechanisms for malfunctioning and, where necessary, adjust units for free mechanical movement.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - Prior to energization of overcurrent protective devices, test devices for continuity of circuitry and current injection for trip tests. Correct malfunctioning units and then demonstrate compliance with the requirements.

- END OF SECTION