- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions, apply to this Section.

      - SUMMARY

        - Section Includes

          - Multicore and single core LV Cables and Wires including, but not limited to, the following:

            - Single core/building wires.

            - Multi-core flexible cables.

            - CU/XLPE/ LSZH insulated cables armoured and Non- armoured.

            - Heat/fire resistant cables.

            - Splices and terminations.

            - Cable markers, supports and ties.

      - REFERENCES

        - BS		            British Standard

        - IEC 228		     Conductors for Insulated Cables.

        - IEC 502           	Extruded Solid Dielectric Insulated Cables for Rated Voltages from 1 kV up to 30 kV.

        - BS 6121		Mechanical Cable Glands (Specifications for).

        - BS 6500		Specification for Insulated Flexible Cords and Cables.

        - BS 7655	Specification for Insulation and Sheathing materials for Cables- PVC sheathing compounds.

        - BS 7671	Requirements for Electrical Installations (IEE Wiring Regulations, 17th Edition: 2008).

        - Local Codes, Regulations and Standards.

      - SUBMITTALS

        - Submit samples of each type of cable proposed.

        - For all types and sizes of LV Cables and Wires, submit the following Manufacturer’s details:

          - Dimensions.

          - Weight.

          - Construction.

          - Current rating.

          - Manner of installation.

          - Maximum conductor operating temperature.

          - Volt drop/amp/meter.

          - Impedance: Separate resistance and reactance values of single and multicore cables.

          - Resistance of armouring in ohms/1000 m length of cable.

          - Characteristic curves for short circuit rating.

          - Minimum bending radius.

        - Submit factory/shop test results showing test voltages, duration of tests and other details for each routine test, in accordance with the requirements of IEC and BS standards. Manufacturer shall submit the results of type tests, if required by the Engineer.

        - Provide samples of all proposed cable types, fittings and related accessories together with the above submittal for approval of the Engineer. It's the contractor's responsibility to get the samples approvals without any extra time extension.

        - Method statement for installation, connection, testing and commissioning of proposed conductors and cables.

      - CLOSEOUT SUBMITTALS

        - Project Record Documents: Record actual locations of components and circuits.

      - QUALITY ASSURANCE

        - Cables and wires shall generally be Manufacturer’s standard construction and materials.

        - All LV cables, wires and accessories furnished under these Specifications shall conform to the applicable standards of Local Standards, IEE, IEC and BS.

      - QUALIFICATIONS

        - Manufacturers: Firms regularly engaged in manufacture of LV cables and wires of the types, sizes and ratings required, whose products have been in satisfactory use in similar service for not less than 10 years.

        - Installer: Firms regularly engaged and qualified with at least 5 years of successful installation experience on projects with electrical installation work similar to that required for the project.

      - FIELD MEASUREMENTS

        - Verify field measurements are as indicated on Drawings.

      - COORDINATION

        - Where wire and cable destination is indicated and routing is not shown, determine routing and lengths required.

        - Wire and cable routing indicated is approximate unless dimensioned.

      - DELIVERY, STORAGE AND HANDLING

        - End of cables shall be sealed to prevent ingress of moisture.

        - Where cables are transported on drums, these shall have adequate circumferences for the cables. Drums shall not be transported on their sides. Each cable drum shall be provided with appropriate weatherproof metallic label indicating project name, order no., type, size and length of the cable delivered. The reels for small building wires shall be provided with appropriate tags indicating at least the type, size and length of wire delivered.

        - After winding on drums, cables shall be protected by being completely enclosed.

        - Care shall be taken during transit to avoid damage to cable and drums.  Before acceptance on site, cable drums and cables shall be inspected for:

          - Damage.

          - Compliance with Specifications.

          - Quantity.

        - Store all LV cables, wires and accessories in factory installed coverings in a clean, dry indoor space which provides protection against the weather and direct exposure to the sun light.

        - As far as possible, each distribution cable shall be supplied in one continuous length without any joint. Where the required run length of any individual cable exceeds the standard/maximum length of a cable drum, as manufactured in the factory, the cables shall be jointed with prior approval of the Engineer using an approved cable joint.

        - Cables shall be handled with care and every effort made to avoid damage to the cable, to other services and to building fabric. Recommendations or instructions available from the cable Manufacturers concerning the installation of cables shall be taken into account. Any damage shall be reported immediately to the Engineer.

        - Cable drums shall be unloaded carefully by means of either a crane or ramp and impact with the ground shall be avoided.  They shall be supported on axles and axle stands while the cable is being pulled; twisting and abrasion of the cable serving or over sheath shall be avoided.

      - SPARE PARTS

        - Furnish extra materials described below that match products installed and that are Packaged with protective covering for storage and identified with labels describing contents.

          - Termination kits: Equal to 2.5% percent of each type of termination kits, cable glands, lugs, ferrules, etc installed but no fewer than two each.

      - MAINTENANCE SERVICE

        - Maintenance Contract: Obtain an undertaking by the equipment manufacturer and his authorized local representative to provide an annual maintenance contract, available after substantial completion of the work, covering routine service and emergency service by trained employees, and to ensure supply of necessary standard spare parts.

        - Initial Maintenance Service: Beginning at Substantial Completion, provide 12 months' full maintenance service by skilled, competent employees of the Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, cleaning, and adjusting as required for proper operation. Use parts and supplies as used in the manufacture and installation of original equipment.

          - Perform maintenance, including emergency callback service, during normal working hours.

          - Include 24-hour-per-day, 7-day-per-week emergency callback service. a. Response Time: 2 hours or less.

      - WARRANTY

        - Submit written guarantee signed by the manufacturer and the contractor for the period of One year from the date of substantial completion. The guarantee shall cover the repair and replacement of defective materials and workmanship as directed by the engineer except where any specific warranty from a supplier or manufacturer extends for a longer time.

      - TRAINING

        - Vendor shall provide operation, maintenance and administration training for the proposed system to Two Engineers. Training shall be sufficient enough to enable the engineers to carry out day-to-day operation, maintenance and operation of the system without or with minimal assistance from the vendor’s technical staff.

- PRODUCTS

      - SINGLE CORE /BUILDING WIRES

        - The conductors of all single core wires shall be of high conductivity, plain, circular, stranded, annealed copper conductors as per IEC 228.

        - The insulation of single core wires shall be heat resistive PVC to BS 7655, Type TI 1 rated at 70 o C for continuous operation.

        - The building wires shall be rated 450/750V.

        - Wires shall be coloured in accordance with section 514 of the IEE Wiring Regulations, 17th Edition (BS 7671).

      - MULTI-CORE FLEXIBLE CABLES

        - Multi-core flexible cables shall be used for the connections of pendant lighting fittings, final equipment connections, portable equipment or any other purpose as shown on the Drawings or approved by the Engineer.

        - The flexible cables shall be of circular construction, rated 300/500 V.

        - The flexible cables shall be of high conductivity, circular, stranded, annealed copper conductors, insulated with heat resistive PVC type 4 to BS 6755, rated at 85oC for continuous operation.

        - Manufacturer shall guarantee that the insulation and overall sheath of the cable will not emit any toxic fumes in the event of a fire.

        - The cores of multi-core flexible cables shall be coloured in accordance with Section 514 of the IEE Wiring Regulations, 17th Edition: 2008 (BS 7671).

      - CU/XLPE/LSZH & CU/XLPE/SWA/LSZH CABLES

        - All low voltage distribution cables shall be copper conductors, 600/1000V grade, cross-linked polyethylene (XLPE) insulated and PVC or polyethylene sheathed cables with Low Smoke Zero Halogen (LSZH) complying with IEC 502.

        - Provide LV distribution cables single-core or multi-core SWA armoured / unarmored as shown on drawings.

        - Cable conductors shall be of high conductivity plain, circular or sector shaped, stranded copper as per IEC 228 and insulated with cross-linked polyethylene (XLPE) rated at 90 oC for continuous operation.

        - The assembly of multi-core armoured cables shall be filled with non-hygroscopic material, compatible with the insulation.

        - Where shown on the Drawings, armoured single-core LV cables shall have non-magnetic armor wire. Single-core cables armoured with steel wire or tape shall not be used for a.c. circuits to prevent eddy (induced) currents. Such conductors shall neither run individually in a ferrous enclosure or pipe nor shall be surrounded by any ferrous material.

        - Armored multi-core LV cables shall be sheathed overall with LSZH Layer.

        - Manufacturer shall warranty that the insulation and overall sheath of the cable will not emit any toxic fumes in the event of a fire.

        - Steel wire armouring of the multi-core armoured cables shall be securely bonded to earth at each termination by means of an adequately sized metallic bond which shall be as short and straight as it is practicable.

        - Cable cores shall be coloured in accordance with section 514 of the IEE Wiring Regulations, 17th Edition (BS 7671).

        - Joints shall not be allowed in any cable, unless a prior written approval of the Engineer is obtained.

      - HEAT/FIRE RESISTANT CABLES

        - For situations, where single or multi-core cables are expected to be in touch with surfaces whose normal working temperature is more than 85 oC (such as light fixtures’ ballast or reflector), or for any other application when specified, special heat resistant cables shall be used.

        - The special PVC insulation of heat resistant cables shall be rated at minimum 150 oC or 10 oC more than the expected surface temperature of the body where cable can touch. Higher of the two values shall be considered for cable insulation temperature rating.

        - Wiring of illuminated exit signs and other emergency lighting fixtures and devices required to work continuously in the event of a fire shall be carried out with special fire resistant cables rated at 900 oC minimum temperature category matching to the rating of other architectural items such as walls, suspended ceiling, etc. in the area.

        - Manufacturer shall warranty that the special insulation of the heat/fire resistant cables will not emit any toxic fumes in the event of a fire.

        - Fire Resistant Copper Cables

          - Fire resistant cables shall be third party approved by LPCB complying to the following:

            - Fire resistant cables shall be certified by the Loss Prevention Certification Board (LPCB).

            - Fire resistant cables shall be in accordance to BS 7629, BS 6387 and IEC 60332 and shall meet the requirements of categories AWX or SWX as a minimum.

            - Cables complying with BS 7629 shall be Type B.

            - Fire resistant cables shall comply with BS 7622 for smoke emission with acid gas emission less than 0.5% when tested to BS 6425-1.

          - Fire resistant cables construction shall include:

            - Conductors:

            - Plain annealed copper to BS 6360 solid (class 1) for 1.5 and 2.5 mm2.

            - Insulation:

            - High performance silicon rubber EL2 to BS 7655: section 1.1

            - Earth Conductor:

            - Tinned annealed copper to BS 6360

            - Electrostatic Screen:

            - Aluminum/polyester tape 125% coverage

            - Sheath:

          - Installation shall be able to withstand fire for the same duration as cables. Type of installation shall be consistent throughout the installation.

          - Fire resistant cables shall be installed in continuous runs without intermediate joints.

          - Fire resistant cables shall be used where prolonged operation during fire is required such as interconnections between detectors, alarm sounders & buzzers, control & indicating equipment & power supplies associated with fire alarm/ fire fighting/ smoke management systems. As well as for emergency escape route lighting installation and as shown on the drawings. Cables shall resist fire for at least 0.5 hour.

          - All joints shall be made in circular conduit boxes complying with B.S.4568, Part 2 or in rectangular adaptable boxes may only be used (after Engineer’s approval) for surface installations. Straight through joints shall not be permitted without the written permission of Engineer.

          - Unless otherwise specified, all conduits, conduit boxes & adaptable boxes shall be galvanized.

      - LOW CURRENT CABLES

        - Provide cables for all low current systems according to the requirements given in the relevant section of each system contained elsewhere in these Specifications. All such cables shall comply with the applicable international standards.

      - SPLICES AND TERMINATIONS

        - Cable splicing or jointing shall not be allowed in any circumstances, except where the required run length of any individual cable exceeds the maximum/standard length as Manufactured in the factory. Obtain Engineer’s written approval for any splice or joint, prior to ordering the cable.

        - Splices and terminations for all LV. cables rated 600/1000 V grade shall be furnished in kit form and shall conform to the recommendations of the cable manufacturer. All material shall be furnished in factory sealed packages and shall not be opened until required for use.

        - Splices for all LV cables shall be pre-molded or heat shrink type and rated for continuous duty at the rating of the services to which they are connected. They shall be suitable for direct buried underground installation or mounted on cable trays as per the requirements on site.

        - Terminations shall be insulated using the materials specified and the procedures recommended by the Manufacturer of the kit being used.

        - Splices for the earth shall be made exothermally or as per the recommendations of the LV cable splice Manufacturer.

      - CABLE MARKERS, SUPPORTS AND TIES

        - Cable markers and identifications discs for all LV cables shall be provided in accordance with the requirements given in Section 26 05 43.

        - Cleats, saddles and clips used for fixing cables shall be black nylon for up to 20 mm dia. cables and glass reinforced nylon for cables above 20 mm dia. All saddles and clips shall be secured using brass round screws for cables up to 20 mm dia. and 10 mm hexagon headed zinc plated bolts and studs above 20 mm dia.

        - All LV cables shall be tied on cable trays/ladders by non-releasing type nylon ties or approved clamps.

        - Clamps for single core cables shall be of non-ferrous material.

- EXECUTION

      - INSPECTION

        - A.	Examine the areas and conditions under which the cables are to be installed and correct any unsatisfactory conditions detrimental to the proper and timely completion of the work. Do not proceed with the work until all unsatisfactory conditions have been corrected in a manner acceptable to the Engineer.

      - SUB-CIRCUIT WIRING INSTALLATION

        - The sub-circuit and final circuit wiring for lighting, small power and equipment power installations shall take the following forms:

          - Single core stranded PVC insulated wires in trunking or conduits for internal wiring.

          - Multi-core XLPE/LSZH insulated unarmored cables in cable trays, ladders or conduits for internal wiring.

          - Multi-core XLPE/SWA/ LSZH insulated armored cables in conduits, cable trays, ladders duct banks or direct buried for external wiring.

        - The types of lighting and small/equipment power installations and accessories are detailed elsewhere in the Specifications and on the Drawings.

        - No conductor smaller than 2.5 mm2 shall be used. Minimum size of direct buried cables whether used for external lighting or any other purpose shall be 4.0 mm2.

        - Each lighting circuit shall be wired using the "loop-in" continuous wiring system and as shown on the Drawings.

        - Small power installations shall be wired using the radial system or ring for special applications as described on the Drawings.

        - Equipment power installations shall generally be wired on a single circuit basis (1-phase or 3-phase), as shown on the Drawings and will serve fixed items of equipment.

        - Each lighting and small/equipment power circuit shall have a separate circuit protective conductor throughout to each light/switch point, power socket outlet or fixed equipment.

        - Where a lighting or small/equipment power circuit is to be installed in trunking or conduit together with any other circuit(s) deviating from drawings, the circuit conductor shall be de-rated for grouping in accordance with table 4B1 of the IEE Wiring Regulations, 17th Edition. This will normally result in the need to increase the conductor sizes as shown in the Panelboard Schedules or on the Drawings.

        - Not more than 2 final sub-circuits shall be run in any conduit.

        - Normal and emergency circuit wiring/cables for lighting, small/equipment power or any other purpose shall be run in separate conduits or in separate compartments of trunking or on separate cable trays/ladders in accordance with IEE Wiring Regulations, 17th Edition.

      - FLEXIBLE CABLE INSTALLATION

        - Flexible cables shall not be concealed directly in any part of the installation except in conduits or sleeves.

        - Where flexible cables are subject to heat they shall be constructed containing a minimum of three cores.

        - All flexible cables are to be of circular construction containing a minimum of three cores.

        - Where portable appliances exceed 200 watt rating, the flexible cable conductor size shall be 1.5 mm2.

        - Flexible cables exceeding 1.5 m in length shall not be allowed, hard wiring shall be taken to within 1.5 m of all equipment or apparatus to be supplied.

      - INTERNAL CABLE INSTALLATION

        - Where cables enclosed in conduits and run vertically in excess of 5 m, the cables shall be clamped to relieve strain on the cables, using suitable approved clamps.

        - Where multiple circuit wiring follows a common route then the wiring shall be installed in trunking rather than multiple conduits with prior approval of the Engineer.

        - Where cables and wires run in trunking, each circuit or group of circuits shall be clipped together using nylon straps or other suitable straps or clips. Vertical runs of trunking exceeding 5 m shall be supplied with pin racks to relieve the strain on cables.

        - All cable runs shall be continuous, no joints will be permitted except where the required run length of an individual cable exceeds the standard/maximum length of a cable drum as manufactured in the factory. Obtain approval of the Engineer for each joint, prior to ordering the cables.

        - Extreme care shall be exercised to prevent tension during bending of LV cables. The permanent radius of cables bend at any location after installation shall not be smaller than the cable Manufacturer’s recommendations.

        - Where cables are supported on cable tray, they shall be fixed to the cable tray using suitable approved straps or clips. Ties shall be spaced at not greater than 600 mm intervals along each cable, and within 100 mm of each bend or set.

        - Where cables are laid on cable trays or ladder in mechanical or electrical rooms or prone to be damaged elsewhere on the project, they shall be mechanically protected by a cover to a height not less than 2 m from the finished floor level.

        - When installing cables, care shall be taken to ensure that electrolytic action does not take

        - Each cable gland shall be from the same Manufacturer as the cable on which it is used and shall be stamped describing the size and number of conductors. PVC shrouds shall be used to protect every gland.

        - Power and lighting cables can be installed on a single cable tray or cable ladder. However normal and emergency power cables shall be installed either on separate cable trays/ladders or separated by mechanical separators if combined on a single cable tray/ladder.

        - TV, Communications and other low current cables shall be installed on separate cable trunking with fire alarm cables separated by mechanical separators from other cables.

      - EXTERNAL CABLE INSTALLATION

        - No work shall commence until the Contractor has investigated the site satisfactorily, and ascertained that the area is free from drains or other underground services. The Contractor shall obtain approval of the routes for external cable with appropriate installation details on shop drawings prior to commencement of any excavation on site.

        - Unless otherwise indicated, excavations within 600 mm of existing services shall be by hand digging. All services uncovered, whether expected or not, shall be reported immediately to the Engineer; they shall be supported by slings or other suitable means and protected. Any damage to services, however minor, shall be reported immediately to the Engineer; no repairs or replacement shall be done unless the Engineer gives his approval.

        - When cable trenches are opened, all cables shall be laid as quickly as possible. The Engineer’s approval shall be obtained before a trench is backfill, generally backfilling shall be commenced within 24 hours of cable laying and the work completed speedily.

        - Keep excavations shall free of water and protected against damage or collapse. The safety of persons and the protection of structures, buildings, roads and services from damage shall be ensured.

        - Before cables are laid, grade bottom of the trench evenly, clean out loose stones and cover for the full width of the trench with a 150 mm layer of sieved sand. Where the level of the trench bottom varies the slope shall not be greater than 1 in 12.

        - Pull cables over cable rollers adequately spaced to prevent the cable being dragged over ground or other surfaces.  For cables pulled into thrust boring or cables ducts and for all cables exceeding 10 m length, use cable stockings for hauling.  Precautions shall be taken to ensure that strain is taken on the cable cores as well as the sheath and excessive strain shall be avoided.

        - After cables have been laid, a further layer of sieved sand shall be added over the full width of the trench and tamped to provide finally not less than 150 mm cover over the cables.

        - Backfill trenches in layers and compact layer before the next layer. The first two layers shall be 100 mm deep and compacted by hand; then mechanical compacting may be used. Cable warning tapes only shall be provided over the external lighting cables, but warning tapes and cable protective tiles shall be used over LV power and MV cables.

        - Warning tapes shall be of polythene not less than 150 mm wide and at least 0.25 mm thick. They shall be yellow in color and bear the continuously repeated legend "-CAUTION ELECTRIC CABLE BELOW" - or similar in English and Arabic, in black letters not less than 30 mm high.

        - Provide cable protective tiles in accordance with the applicable regulations and standards. Cable protective tiles shall be placed directly on the compacted sand cover over the cables.

        - Where cables laid in trenches and cross other cables; a minimum clearance of 250 mm between the crossing cables shall be maintained. Cables shall not be laid one above the other except where shown on the Drawings.

        - If more than one cable is to be drawn in a duct, all such cables shall be bunched together and pulled in one operation, wherever possible.

        - Where cables run under roadways, install in PVC ducts encased in concrete. The ducts shall extend for a minimum distance of 1 m on each side of roadway and shall be sealed at each end.

        - Ducts shall be sized to allow installation of cable without excessive tension loads. 20% spare ducts shall be provided with a minimum of one spare duct at each location.

        - When installed in cable ducts, all multi-core cables shall be installed singly and continuous between the manholes. Splicing of cables between the manholes shall not be allowed in any case.

        - For cables pulled into thrust borings or cable ducts exceeding 10 m length, use cable stockings for hauling.  Precautions shall be taken to ensure that strain is taken on the cable cores as well as on the sheath. The pulling tension of the cable shall not exceed the maximum tension recommended by the cable Manufacturer.

        - Utilize both manual and power type pulling mechanisms on site as required with the rated capacity (in kilograms or pounds) clearly marked on the mechanism. A dynamometer shall be used to show the tension on the cable during all pulls and the indicator shall be constantly watched. If any excessive strain develops, the pulling operation shall be stopped at once and the difficulty determined and corrected. The dynamometer shall have a maximum tension indicator to show the maximum tension developed during a pull. The cable play-out reel shall be equipped with a suitable brake and shall be constantly manned during all pulls.

        - Under no circumstances shall cable be pulled using equipment not monitored by a dynamometer. The use of motor vehicles in pulling cable is prohibited. Any cable so pulled shall be removed and replaced.

        - To avoid insulation damage from excessive sidewall pressure at bends in raceway runs, the pulling tension in the cable in kilograms as it leaves the bend shall not exceed 500 times the radius of the bend in meters.

        - Support cables at all times without excessive sag.  Cables shall be located in such a way as to minimize interference with other cables to be installed.

        - Provide adequate length of cables in manholes to avoid distorting pressures on the cables at conduit bushings. Cable protection such as a layer of light rubber belting, friction tape or similar material shall be provided where required before permanently fixing the cables in place.

        - Install and support cables in such a way that there shall be no undue mechanical strain on the cable terminations. The requirements of the IEE Wiring Regulations, 17th Edition, chapter 52 shall be fulfilled for the erection of LV cables, as applicable.

        - Terminate cables using only the correct size and type of gland with earth tag and PVC shroud, as supplied or recommended by the cable Manufacturer. All glands shall be dustproof and the glands for outdoor usage shall be fully weather and waterproof.

        - Bend cable armoring to earth at each termination by means of a green/yellow Cu/PVC earth conductor, sized in accordance with Section 543 of the IEE Wiring Regulations, 17th Edition, connecting the cable gland earth tag to the local earth terminal.  The apparatus gland plate shall be cleaned to bare metal around the cable gland earth tag bolted connection to ensure a sound electrical connection.

        - Where cables pass through walls or floors, protect by PVC or mild steel sealed sleeves cast into the building fabric. If the walls or floors are fire divisions, then the sleeves shall be fire stopped after installation of the cable(s) to the same rating as the walls or floors through which they pass.

        - Before any tradesman is allowed to terminate an armored cable in the permanent works, he shall make a demonstration termination in the presence of the Engineer and obtain the approval of the Engineer.

        - Where cables pass through ducts or sleeves entering buildings, seal the ends of the ducts or sleeves using a special caulking compound of a putty-like consistency. It shall be workable with the hands at temperatures as low as 1.7 oC, and shall not slump up to a temperature of 149 oC or less. It shall not be hardened materially when exposed to air.

        - Install cable markers and identification discs in accordance with the requirements given in Section 26 05 53 and locate them so that they are readily visible when cable is permanently fixed in position.

      - SPLICING AND TERMINATIONS

        - Cable splicing or jointing is not allowed, except where the required run length of any individual cable exceeds the maximum/standard length as manufactured in the factory. The Contractor shall obtain Engineer’s written approval for any splice or joint, prior to ordering the cable.

        - The Engineer shall be informed whenever cables are to be spliced or terminated.

        - The Engineer shall be given evidence that the joint or termination Manufacturer has stated that materials to be employed are suitable for the type of cable to be jointed or terminated.

        - Supply and install all materials, equipment and accessories necessary for the proper jointing, terminating and connecting, ready for service, of all cables included in the works.

        - Employ for this work, staff who are fully qualified and competent for the types of joints and terminations to be made.

        - Take all necessary precautions to prevent damage and ingress of moisture and impurities; cables ends shall be made free from moisture before jointing commences. Where circumstances prevent completion of the jointing or termination, the cable ends shall be sealed properly.

        - All jointing and terminations, once commenced, shall proceed continuously until it is completed and sealed in the shortest possible time, without interruption.  No terminations shall be made under wet or dirty conditions.

        - Terminate all cables in brass compression glands complying with BS 6121 and of a design appropriate to the type and size of cable(s) being terminated. Glands for armoured cables shall be provided with a properly designed clamping device for the armour or screen. All cable glands shall be provided with a dust and waterproof outer sheath seal.

        - Provide compression glands with earthing tags and close-fitting PVC shrouds.

        - Except where it is impracticable to do so, the cable cores shall be taken through the terminating box directly to the terminals of the equipment, without crosses, and shall be made off with an approved type of hydraulically crimped socket.

        - The cores of all cables shall be correctly 'phased out' before the final jointing, terminations or connections are made. Continuity of spare cores shall be maintained at joints. At terminations, any spare cores shall be connected to spare terminals.

        - At all cable terminations the armoring or metallic sheath of the cables, if any, shall be solidly bonded to the equipment earth terminal or bar by means of properly designed brass or copper clamps and a copper conductor of section not less than that required by the IEE Wiring Regulations, subject to a minimum section of 2.5 mm².

        - Core identification at terminations shall be done by colored or numbered plastic stretch or shrink ferrules.

        - Utilize appropriate crimping tools for splicing and termination of all cables with guides to position the connectors or lugs in the tool correctly. The connectors, lugs and associated dies for the compression tool shall be of correct type and size. The crimping tool shall be designed with steps to prevent over crimping and shall be of a type which have provision to prevent the tool from opening until the crimp action is completed.

        - Tools for manipulation and termination of cables shall be of a design approved by the cable Manufacturer. Corrugation of the metal sheath or damage to outer coverings will not be accepted. A wood block or wooden faced tool shall be used to finally dress the cable into position.

        - Repairs to a cable sheath, regardless of the extent of the damage, will not be accepted; straight through joints only are permitted.

        - Splices shall not be made to utilize short lengths of cable. When cables being installed into a duct system with manholes, the splices shall only be provided within manholes and no splice shall be allowed outside the manholes.

        - Jointing and terminations shall be made in accordance with the Manufacturer's instructions.

        - The sleeves used for jointing and terminations shall be shrink type, applied cold or by the use of heat. They shall provide a sufficient thickness of insulation to suit the particular application.

        - The insulation tapes used for jointing and terminations shall have temperature rating and insulating property not less than the cable insulation. They shall be fully compatible with the type and size of cables and comply with the applicable standards and regulations.

      - FIELD QUALITY CONTROL

        - Comply with Section 26 01 26.

        - All LV cables and wires shall be tested when splicing and terminations are fully prepared and completed, except for final connections of cables/wires tails onto equipment.

        - Test each conductor for phasing, continuity and insulation resistance (meggar).

        - After completion of the installation of L.V. cables and wires, carry out insulation resistance test for 1 minute at 500 V or 1000 V, according to the rated voltage of the cables/wires under test. The test voltage shall be applied between the conductors and between each conductor and earth/neutral and shall comply with the requirements of IEE Wiring Regulations, 17th edition and other applicable standards.

      - SLEEVE-SEAL INSTALLATION

        - Install to seal underground exterior-wall penetrations.

        - Use type and number of sealing elements recommended by manufacturer for cable material and size. Position cable in center of sleeve. Assemble mechanical sleeve seals and install in annular space between cable and sleeve. Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

      - FIRESTOPPING

        - Apply fire stopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly according to Section 078400 "Fire Stopping."

- END OF SECTION